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[bookmark: _Toc438666677][bookmark: _Toc233209860]Introduction and Instructions
[bookmark: _Toc438666678]
USE AND LIMITATIONS
[bookmark: _Toc438666679]These model green building specifications have been developed for informational purposes only to support the preparation of project-specific construction documents. They are intended as examples only and do not constitute professional, engineering, architectural, legal, or regulatory advice. Further, the Submittal provisions in this resource do not represent the project submittals required for certification under the 2026 Enterprise Green Communities Criteria. Refer to Green Communities program documents for a list of submittals required for certification. Project teams may elect to include or remove suggested submittals in these specifications based on contractors’ experience with different systems and technologies. Green Communities urges project teams to require photo documentation for any systems which are critical to the project’s overall performance and/or unfamiliar to the construction team. 
The specifications are not a substitute for the independent judgment of qualified design, construction, legal, or procurement professionals. Users are solely responsible for reviewing, modifying, and adapting the specifications to address project-specific conditions, applicable laws, regulations, codes, standards, procurement requirements, and owner objectives.
Enterprise makes no representations or warranties regarding the accuracy, completeness, suitability, or fitness of the specifications for any particular purpose and assumes no responsibility or liability for any outcomes resulting from their use. Reference to any product, technology, manufacturer, certification, or standard does not constitute an endorsement.
Use of these model specifications is entirely at the user's own risk.

TEMPLATE SPECIFICATIONS (WORD)
This editable Word document is organized according to MasterSpec standard Divisions. All specifications for the 2026 Criteria are written into Division 1: General Requirements, Section 01 81 13 Sustainable Building Requirements. The remaining MasterSpec Divisions reference the appropriate green specification under Section 01 81 13. 
[bookmark: _Toc438666680]


SPECIFICATIONS TOOL FOR THE 2026 CRITERIA (EXCEL)
The Specifications Tool is an editable Excel file that provides several supporting features to this Word document or can be used as a replacement for this Word document. There are more details within the Excel file explaining how to use the Excel tool to generate customized template specifications based on project-specific inputs. Aside from the ability to generate customized specifications, the Specifications Tool also provides the following features to support users of the Word-based Template Specifications:
· A form that walks through each decision the project team needs to make in order to customize the specifications appropriately based on project parameters.
· A matrix (chart) that maps each Green Communities criterion to relevant MasterSpec sections contained within the template specifications. The matrix also notes whether the criterion results in specifications for Submittals, Products, and/or Execution. This matrix can serve as a tool to help project teams to quickly visualize which MasterSpec sections can be removed, or need to be retained, based on project parameters.
[bookmark: _Toc438666681]
INTEGRATING THE WORD AND EXCEL TOOLS
Design teams can copy, paste, and edit the Template Specifications (Word) to suit their needs. If a team elects to use the Template Specifications, they may benefit from integrating the Excel Specifications Tool as follows: 
1. Fill out the Criteria Selection Tab in the Excel Tool to understand which rows of the criteria matrix are applicable to the project.
2. Use the Filter column to show only the line items marked "Show" and hide all others.
3. Delete all MasterSpec sections from the Template Specifications that no longer have an "X" marked in any row of the matrix. 
4. Using the completed form on the Criteria Selection Tab and the comment boxes in the Template Specifications, delete any specifications within 01 81 13 that do not apply to the project.



LEGEND FOR SPECIFICATION EDITS 
	MasterSpec Division
	Division 1: General Requirements

	MasterSpec Section
	01 81 13 / SUSTAINABILITY REQUIREMENTS

	Comments describe edits required based on project parameters
	Comments are present throughout Section 01 81 13. For all other sections, reference comments within 01 81 13 to determine if specifications apply.

	Green Communities Mandatory Criterion
	Specifications with headings that have no comments or color coding (throughout Section 01 81 13) are always required.

	Green Communities Mandatory or Optional Criterion, depending on project parameters
	Where a Green Communities criterion is sometimes optional, depending on project parameters (e.g., Rehab vs. New Construction), the heading for the criterion is written in this color (throughout Section 01 81 13 only).

	Green Communities Optional Criterion
	Where a Green Communities Criterion is always optional, the heading for the criterion is written in this color (throughout Section 01 81 13 only).

	Choices required based on project parameters or options selected under a Criterion
	Where a Green Communities Criterion has multiple options that result in different specifications within the criterion, headings for each Option, or edits required within a specification, are written in this color (throughout Section 01 81 13 only).





[bookmark: _Toc233209861]Division 1: General Requirements
[bookmark: _Toc233209862]01 42 00 / References
PART 1 - GENERAL
1.1 Related Sections
Section 01 81 13 Sustainability Requirements
1.2  References
1. Air Conditioning Contractors of America (ACCA) Manuals J and S
American Society of Civil Engineers, Flood Resistant Design and Construction, ASCE/SEI 24-24
American Society of Civil Engineers, Supplement 2 of ASCE/SEI 7-22: Minimum Design Loads and Associated Criteria for Buildings and Other Structures
ANSI/ASHRAE Standard 62.1-2022—Ventilation and Acceptable Indoor Air Quality, Section 5.2
ANSI/ASHRAE Standard 62.2-2022, Ventilation and Acceptable Indoor Air Quality in Residential Buildings, sections 5 and 7
ANSI/RESNET/ICC 301, Standard for the Calculation and Labeling of the Energy Performance of Dwelling and Sleeping Units using an Energy Rating Index (Standard 301)
ANSI-AARST MAH-2023, Protocol for Conducting Measurements of Radon and Radon Decay Products in Homes
ANSI-AARST MA-MFLB-2023, Protocol for Conducting Measurements of Radon and Radon Decay Products in Multifamily, School, Commercial and Mixed-Use Buildings
ANSI-AARST SGM-MFLB-2023, Soil Gas Mitigation Standards for Existing Multifamily, School, Commercial and Mixed-Use Buildings
ASHRAE Handbook—Fundamentals
ASHRAE Standard 90.1-2013, Energy Standard for Sites and Buildings Except Low-Rise Residential Buildings, Appendix G of 90.1-2016
ASTM C1288, Standard Specification for Fiber-Cement Interior Substrate Sheets
Athena Impact 
1. BPI Combustion Appliance and Fuel Distribution System Inspection
Builders for Climate Action, BEAM Estimator
Building Transparency, EC3 Embodied Carbon in Construction Calculator
C.Scale
California Air Resources Board (CARB) Phase II Composite Wood Products Airborne Toxic Control Measure
California Department of Public Health (CDHP), Standard Method for the Testing and Evaluation of Volatile Organic Chemical Emissions from Indoor Sources using Environmental Chambers, Version 1.2
Carbon Leadership Forum (CLF), 2025 CLF North American Material Baselines
DarkSky Luminaires Program Version 3.0
Ecotope, Ecosizer
Federal Communications Commission, National Broadband Map
Federal Geographic Data Committee, Classification of Wetlands and Deepwater Habitats of the United States
Florida Fish and Wildlife Conservation Commission (FWC) Guidelines
Forest Stewardship Council (FSC) Standard
Habitable, Informed Screening Tool
Illuminating Engineering Society and DarkSky International, Joint IDA – IES Model Lighting Ordinance (MLO)
Insurance Institute for Home & Business Safety (IBHS), FORITIFIED: Roof, Silver, Gold, Hail Supplement
International Association of Plumbing and Mechanical Officials (IAPMO), Water Demand Calculator
International Code Council (ICC), ICC G2-2010 Guideline for Acoustics
International Code Council, 2024 International WUI Code
International Code Council, CSA B805/ICC 805:2022, Rainwater Harvesting Systems.
International Energy Conservation Code (IECC) 2018, Figure 301.1: Climate Zone Map
International Residential Code (IRC) 2009, Table M1507.3
ISO 8336 (Fibre-cement flat sheets—Product specification and test methods
Louisiana State University AgCenter, ASCE Elevation Calculation Tool
mindful MATERIALS, Common Materials Framework (CMF) Reference Guide
Multifamily Home Energy Retrofit Coordinating Committee (MF HERCC) Combustion Safety Testing Protocols for Existing Multifamily Buildings
National Fire Protection Association (NFPA) 10, Standard for Emergency and Standby Power Systems
National Fire Protection Association (NFPA) 
1. Standard 72, National Fire Alarm and Signaling Code
2. Standard 1140, Wildland Fire Protection
National Green Building Standard (NGBS), Water Rating Index (WRI)
National Wildlife Coordinating Group, NWCG Standards for Mitigation in the Wildland Urban Interface
NBBJ, ZeroGuide
NSF International, Certified Product Listings for Lead Reduction.
NSF/ANSI
3. Standard 53, Drinking Water Treatment Units, Health Effects
4. Standard 58, Reverse Osmosis Drinking Water Treatment Systems
5. Standard 61, Drinking Water System Components – Health Effects
One Click LCA, Carbon Designer 3D (CD3D)
Passive House International (PHI, Classic, Plus, Premium, LEB, EnerPHit
Payette, Kaleidoscope: Embodied Carbon Design Tool
Phius Certification Guidebook, CORE, ZERO, and REVIVE
RESNET Standard for Combustion Safety Testing and Work Scope
RESNET, Water Efficiency Rating System HERSH2O
SGM-SF-2023— Soil Gas Mitigation Standards for Existing Homes
South Coast Air Quality Management District (SCAQMD)
6. Rule 1113: Architectural Coatings
7. Rule 1168: Adhesive and Sealant Applications
State of California, Building Energy Efficiency Standards (Title 24)
Tally (software)
Toxic Substances Control Act (TSCA) Title IV
U.S. Army Corps of Engineers, Regional Supplements to Corps Delineation Manual
U.S. Department of Energy, DOE Efficient New Homes Multifamily National Program Requirements, Version 2
U.S. Department of Homeland Security, FEMA Flood Map Service Center
U.S. Department of Housing and Urban Development (HUD)
8. Noise Abatement and Control. Regulation 24 CFR Part 51, Subpart B
9. Notice H2015-04, Part VI: Assisted Housing Utility Allowance Calculations sampling protocol
10. Designing for Natural Hazards: A Resilience Guide for Builders & Developers, Volume 1: Wind
11. Designing for Natural Hazards: A Resilience Guide for Builders & Developers, Volume 2: Water
U.S. Environmental Protection Agency (EPA) 
12. Technical Guidance on Implementing the Stormwater Runoff Requirements for Federal Projects under Section 438 of the Energy Independence and Security Act
13. ENERGY STAR NextGen Program
14. ENERGY STAR Residential New Construction Program
15. Indoor AirPlus
16. Lead Abatement, Inspection, and Risk Assessment
17. Lead and Copper Rule
18. National Pollutant Discharge Elimination System (NPDES) Construction General Permit for Stormwater Discharges
19. National Primary Drinking Water Regulations
20. Radon Zone Map
21. WaterSense Labeled Homes Version 2.0
22. ENERGY STAR Portfolio Manager
U.S. Federal Emergency Management Agency (FEMA), Building Designer’s Guide to Calculating Flood Loads Using ASCE 7-22 Supplement 2 (FEMA P-2345/April 2024)
Uniform Plumbing Code (UPC) 2024, Appendix M: Peak Water Demand Calculator
Water Efficiency Rating Score (WERS)

[bookmark: _Toc233209863]01 42 13 / Abbreviations and Acronyms
PART 1 - GENERAL
1.1 Related Sections
1. Section 01 81 13 Sustainability Requirements
1.2  Abbreviations and Acronyms
1. ACCA: Air Conditioning Contractors of America
ACH: Air changes per hour
AIIC: Apparent Impact Insulation Class
ALMS: Automatic load management system
APEs: Alkylphenol ethoxylates
ASCE: American Society of Civil Engineers
ASTC: Apparent Sound Transmission Class
AWG: American wire gauge
BFE: Baseline flood elevation
BUG: Backlight, Uplight, Glare
CARB: California Air Resources Board
CDPH: California Department of Public Health
CFM: Cubic feet per minute
CFM50/sfbe: Cubic feet per minute at 50 Pascals per square foot of building enclosure
CFU/mL: Colony forming units per milliliter (E. coli)
CLT: Cross-laminated timber
CMF: Common Materials Framework
CO: Carbon monoxide
DFE: Design flood elevation
EC3: Embodied Carbon in Construction Calculator
EPA: Environmental Protection Agency
EPD: Environmental Product Declaration
ERI: Energy Rating Index
ERV: Energy recovery ventilator
EV: Electric vehicle
EVSE: Electric vehicle supple equipment
FEMA: Federal Emergency Management Agency
FSC: Forest Stewardship Council
FT Agent: Functional Testing Agent (HVAC)
FWC: Florida Fish and Wildlife Conservation Commission
gpc: Gallons per cycle
gpf: Gallons per flush
gpm: Gallons per minute
GWP: Global warming potential
HPWH: Heat pump water heater
HRV: Heat recovery ventilator
HUD: Department of Housing and Urban Development
IAPMO: International Association of Plumbing and Mechanical Officials 
IECC: International Energy Conservation Code
IIC: Impact Insulation Class
IPM: Integrated pest management
IWF: Integrated water factor
kW: Kilowatts
LED: Light-emitting diode
LZ: Lighting Zone
MDF: Medium-density fiberboard
MERV: Minimum Efficiency Reporting Value (air filtration)
mg/L: Milligrams per liter
MLO: Model Lighting Ordinance
NAF: No added formaldehyde
NFPA: National Fire Protection Association
NPDES: National Pollutant Discharge Elimination System
OITC: Outdoor-Indoor Transmission Class
PFAS: Per- and polyfluoroakyl substances
PSI: Pounds per square inch
PV: Photovoltaic
RECs: Renewable energy certificates
RL: Repetitive loss (flood)
SCAQMD: South Coast Air Quality management District
SFHA: Special Flood Hazard Area
SR: Solar reflectance
SRI: Solar reflectance index
SRL: Severe repetitive loss (flood)
STC: Sound Transmission Class
TSCA: Toxic Substances Control Act
UEF: Uniform Energy Factor
UPC: Uniform Plumbing Code
V: Volts
VOC: Volatile organic compounds 

[bookmark: _Toc233209864]01 42 16 / Definitions
PART 1 - GENERAL
1.1 Related Sections
1. Section 01 81 13 Sustainability Requirements

1.2  Definitions
1. Albedo
1. The ability of a surface to reflect solar radiation. Higher albedo materials are typically lighter in color and provide superior reflection than darker materials.
Backlight
2. For an exterior luminaire, lumens emitted in the quarter sphere below horizontal and in the opposite direction of the intended orientation of the luminaire. For luminaires with symmetric distribution, backlight will be the same as front light.
Base Flood Elevation 
3. The height floodwaters are predicted to reach during a 100-year flood event, commonly used while evaluating flood risk.
BUG
4. A luminaire classification system that classifies backlight (B), uplight (U) and glare (G).
Design Flood Elevation
5. The minimum elevation to which a structure must be elevated or floodproofed, as set and regulated by local authorities.
EV-Capable
6. A parking space is considered EV capable when it has electrical capacity and conduit installed to support a Level 2 EV charger but lacks the wiring and outlet.
EV-Ready
7. A parking space is considered EV ready when it has all components wired and installed to support a Level 2 EV charger but lacks the charger itself. 
Freeboard
8. The additional height above base flood elevation (BFE) protecting a building from flooding, usually 1 to 3 feet for critical facilities.
Glare
9. Lighting entering the eye directly from luminaires or indirectly from reflective surfaces that causes visual discomfort or reduced visibility.
Hurricane-Prone Regions (for FORTIFIED program)
10. Areas vulnerable to hurricanes as defined in ASCE. For ASCE 7-10, ASCE 7-16, and ASCE 7-22, hurricane-prone regions are locations along the Gulf of Mexico and Atlantic coasts where the wind speed for Risk Category II buildings is greater than 115 mph, plus Hawaii, Puerto Rico, the Virgin Islands, Guam, and American Samoa.
LED (Light-Emitting Diode)
11. Energy-efficient lights that produce less initial heat per lumen, consume less energy, and last longer than conventional incandescent and fluorescent lights
Potable Water
12. Water suitable for drinking and supplied from wells or municipal water systems.
Property Line
13. When establishing requirements for exterior lighting BUG ratings, allow extra 5 feet when property line abuts public walkway, bikeway, plaza, and parking lot. For property lines that abut public roadways and public transit corridors, property line considered to be the centerline of the public roadway or corridor.
Radon
14. Colorless, odorless, and tasteless gas that can greatly affect indoor environmental health. According to the EPA, radon exposure is the second leading cause of lung cancer in the US
Sediment
15. Soil and other debris that has been eroded and transported by storm or production runoff water.
Solar Reflectance (Albedo)
16. The measure of a material’s ability to reject solar heat, as shown by a small temperature rise. Calculated according to ASTM E1980 using the material’s Emittance and Reflectivity values. Standard black has an SRI of 0 and standard white has an SRI of 100.
Uplight
17. For an exterior luminaire, flux radiated in the hemisphere at or above the horizontal plane.

[bookmark: _Toc233209865]01 43 00 / Quality Assurance
PART 1 - GENERAL
1.1  Summary
1. This section includes credentials required to comply with 2026 Green Communities Criteria.
1. Related Sections
7. Section 01 81 13 Sustainability Requirements
1.2  Definitions
1. Criterion 3.5: Outdoor Water Use: Efficient Irrigation	
8. EPA WaterSense Certified Irrigation Auditor
1. A Certified Auditor must program and commission the irrigation system.
1. Criterion 3.6 Outdoor Water Use: Alternative Sources	
9. Professional certified by the American Rainwater Catchment Systems Association or equivalent
1. A Certified Professional must design the irrigation system that uses rainwater for irrigation.
1. Criterion 5.2a: Building Performance - New Construction	
10. Raters, ASHRAE Path Energy Modelers, and Functional Testing Agents (FT Agents) must be eligible to provide services under the ENERGY STAR program.
1. Eligible raters and/or FT agents must complete all required verifications per the ENERGY STAR program.
10. Energy raters must be qualified per ANSI/RESNET/ICC 301.
1. Criterion 5.3: Advanced Building Performance	
11. Raters, ASHRAE Path Energy Modelers, and Functional Testing Agents (FT Agents) must be eligible to provide services under the DOE Efficient New Homes program.
1. Eligible raters and/or FT agents must complete all required verifications per the DOE Efficient New Homes program.
11. Raters must be eligible to provide services under the ENERGY STAR NextGen program.
2. Eligible raters must complete all required verifications per the ENERGY STAR NextGen program.
11. Accredited Passive House Institute Building Certifier
3. An accredited certifier must verify features for any PHI certifications including Classic, Plus, Premium, LEB, and EnerPHit.
11. Phius Certified Consultant (CPHC)
4. A certified consultant must verify features for any Phius certifications including CORE, ZERO, and REVIVE.
1. Criterion 7.1: Clean Air - Radon Testing and Mitigation	
12. A radon professional must supervise radon testing.
12. Radon professionals must have Certification/license from the state in which the testing or mitigation work is being conducted, if the state has this requirement, and one of the following:
2. Certification from the American Association of Radon Scientists and Technologists’ (AARST) National Radon Proficiency Program (NRPP)
2. Certification from the National Radon Safety Board (NRSB)"


[bookmark: _Toc233209866]01 45 29 / Testing Laboratory Services
PART 1 - GENERAL
1.1  Summary
1. Related Sections
13. Section 01 81 13 Sustainability Requirements
1.2  Submittals
1. 2026 Green Communities Criterion 4.3: Water Quality
14. Submit documentation in accordance with 01 81 13 under Criterion 4.3.
1. 2026 Green Communities Criterion 7.1 Clean Air: Radon Testing and Mitigation
15. Submit documentation in accordance with 01 81 13 under Criterion 7.1.
Part 2 - Products
2.1 Product Requirements
1. 2026 Green Communities Criterion 4.3: Water Quality
1. Provide products in accordance with 01 81 13 under Criterion 4.3.
Part 3 - Execution
3.1 Execution Requirements
1. 2026 Green Communities Criterion 4.3: Water Quality
17. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.3.
1. 2026 Green Communities Criterion 7.1 Clean Air: Radon Testing and Mitigation
18. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.1.

[bookmark: _Toc233209867]01 56 16 / Temporary Dust Barriers	Comment by Customization Instructions: Retain if project is using Criterion 7.7, Option 1: Management of construction pollution, to earn optional points.
Part 1 - General
1.1  Summary 
1. Related Sections
19. Section 01 81 13 Sustainability Requirements
1.2 Submittals
1. 2026 Green Communities Criterion 7.7 Clean Air: Enhanced IAQ
1. Submit documentation in accordance with 01 81 13 under Criterion 7.7.
Part 2 - Products
2.1 Product Requirements
1. 2026 Green Communities Criterion 7.7 Clean Air: Enhanced IAQ
21. Provide products in accordance with 01 81 13 under Criterion 7.7.
Part 3 - Execution 
3.1 Execution Requirements
1. 2026 Green Communities Criterion 7.7 Clean Air: Enhanced IAQ
22. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.7.

[bookmark: _Toc233209868]01 57 13 / Temporary Erosion and Sediment Control
PART 1 - GENERAL 
1.1  Summary 
1. Related Sections
23. Section 01 81 13 Sustainability Requirements
1.2  Submittals
1. 2026 Green Communities Criteria 3.1: Minimization of Disturbance During Staging and Construction
24. Submit documentation in accordance with 01 81 13 under Criterion 3.1.

PART 2 - PRODUCTS (no Green Communities Requirements)
PART 3 - EXECUTION 
3.1  Execution Requirements
1. 2026 Green Communities Criteria 3.1: Minimization of Disturbance During Staging and Construction
25. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.1.

[bookmark: _Toc233209869]01 74 19 / Construction Waste Management and Disposal	Comment by Customization Instructions: Retain if Criterion 6.2, Strategy G or H is used.
Part 1 – General
1.1 Summary
1. Related Sections	
26. Section 01 81 13 Sustainability Requirements

1.2  Submittals	
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.2.

Part 2 – Products (no Green Communities Requirements)		
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.

[bookmark: _Toc233209870]01 78 23 / Operations and Maintenance Data		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2 Submittals		
1. 2026 Green Communities Criterion 8.1 Building Operations and Maintenance Manual and Plan
30. Submit documentation in accordance with 01 81 13 under Criterion 8.1.
1. 2026 Green Communities Criterion 8.2: Emergency Management Manual
31. Submit documentation in accordance with 01 81 13 under Criterion 8.2.
Part 2 – Products (no Green Communities Requirements)			
Part 3 – Execution (no Green Communities Requirements)		

[bookmark: _Toc233209871]01 78 53 / Sustainable Design Closeout Documentation			Comment by Customization Instructions: Retain if project is:
1. New Construction
2. Substantial or Moderate rehab, and Criterion 5.3 is selected to earn optional points.
Part 1 - General				
1.1  Summary		
1. Related Sections	
32. Section 01 81 13  Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
33. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
1. 2026 Green Communities Criterion 5.3: Building Performance - Advanced Building Performance
34. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
Part 2 - Products				
2.1  Product Requirements		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction
35. Provide products in accordance with 01 81 13 under Criterion 5.2a.
1. 2026 Green Communities Criterion 5.3: Building Performance - Advanced Building Performance	
36. Provide products in accordance with 01 81 13 under Criterion 5.3.
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
37. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
1. 2026 Green Communities Criterion 5.3: Building Performance - Advanced Building Performance
38. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3.	

[bookmark: _Toc233209872]01 79 00 / Demonstration and Training		
Part 1 - General				
1.1  Summary		
1. Related Sections	
39. Section 01 81 13  Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 1.4: Construction Management	
40. Submit documentation in accordance with 01 81 13 under Criterion 1.4.
1. 2026 Green Communities Criterion 8.4: Walk-Throughs and Orientations to Property Operation	
41. Submit documentation in accordance with 01 81 13 under Criterion 8.4
Part 2 – Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 1.4: Construction Management	
42. Conform to execution requirements in accordance with 01 81 13 under Criterion 1.4
1. 2026 Green Communities Criterion 8.4: Walk-Throughs and Orientations to Property Operation
43. Conform to execution requirements in accordance with 01 81 13 under Criterion 8.4

[bookmark: _Toc233209873]01 81 13 / Sustainability Requirements		
[bookmark: _Toc233209874]Part 1 - General				
1.1  Summary			
1. Section Includes: 
44. Summary of sustainable building requirements for project as necessary for certification of this project through the 2026 Green Communities Criteria. 
44. Related performance and administrative requirements. 
Related Sections within Division 01:	 General Requirements	
Requirements are not repeated but 01 81 13 is referenced within respective sections.
3. Section 01 42 00 References
4. Section 01 42 13 Abbreviations and Acronyms
5. Section 01 42 16 Definitions
6. Section 01 43 00 Quality Assurance
7. Section 01 45 29 Testing Laboratory Services
8. Section 01 56 16 Temporary Dust Barriers
9. Section 01 57 13 Temporary Erosion and Sedimentation Control
10. Section 01 74 19  Construction Waste Management and Disposal
11. Section 01 78 23 Operations and Maintenance Data
12. Section 01 78 53 Sustainable Design Closeout Documentation
13. Section 01 79 00 Demonstration and Training
14. Section 01 91 00 Commissioning
15. Section 01 92 13 Facility Operation Procedures
16. Section 01 93 13 Facility Maintenance Procedures
Other related Divisions: 
Requirements are not repeated but 01 81 13 is referenced within respective sections.  	
Divisions 02 - 12, 14, 22, 23, 26 - 28, and 31 - 34 where related submittal, product, or execution requirements relate to Criteria.  
1.2  References			
1. 2026 Enterprise Green Communities Criteria		
Refer to 01 42 00 for a comprehensive list of References and Definitions		
1.3  Coordination			
1. Contractor is responsible for all requirements of the 2026 Criteria that are contained throughout these Specifications, including successful compliance with and passage of visual inspections and performance tests by verifying party.
Lead testing and remediation: Contractor is responsible to ensure lead testing is executed, as applicable, prior to installation of remediation measures as required by the 2026 Criteria.
ENERGY STAR verification: Contractor is responsible for coordinating with appropriate verification team members to ensure inspections and leakage tests can be performed at the appropriate times and without delaying construction progress.
Coordinate framers, plumbers, HVAC, insulators, and drywall trades to minimize uncontrolled air leakage pathways between residential units by sealing all penetrations in walls, ceilings, and floors in the units and by sealing all vertical chases adjacent to the units.  
1.4  Submittals
1. Location and Neighborhood Fabric 
1. Criterion 2.1: Ecological Conservation and Safer Sites
a. Attestation and documentation, as required by the project team, that the as-built project meets ASCE 24-24.	Comment by Customization Instructions: Retain if project is a substantial rehab located in a special flood hazard area. 	Comment by Customization Instructions: NYC Overlay: Delete item a.
b. Submit pre-build and as-built photo documentation showing extent of structures, roads, and parking areas before and after construction. 	Comment by Customization Instructions: Retain if project is:
Substantial or Moderate Rehab located in an aquatic ecosystem
2. Criterion 2.6: Transit, Mobility, and Walkability	Comment by Customization Instructions: Retain if 2.6 Increased Bikeability - Long-Term Bike Storage is selected for points.
a. Product data and/or photo documentation of long-term bicycle storage.
Site Design
3. Criterion 3.1: Minimization of Disturbance During Staging and Construction	Comment by Customization Instructions: NYC Overlay: Delete this Criterion.
a. Submit photo documentation showing implementation of erosion and sedimentation control plan throughout construction.	Comment by Customization Instructions: Applies to projects 1 acre or smaller.
b. Submit photo documentation showing implementation throughout construction of 2022 U.S. Environmental Protection Agency (EPA) National Pollutant Discharge Elimination System (NPDES) Construction General Permit for Stormwater Discharges, or documentation as required by project team.	Comment by Customization Instructions: Applies to projects larger than 1 acre.
4. Criterion 3.2: Site Design for Ecosystem Services
a. Submit product data for plantings.
5. Criterion 3.3: Exterior Lighting	Comment by Customization Instructions: Delete Criterion 3.3 if scope does not include exterior lighting.
a. Submit product data for all exterior lighting fixtures and luminaries, documenting lumens and Backlight, Uplight, and Glare (BUG) ratings.
b. Submit photo documentation showing mounting heights of all exterior lighting fixtures.
c. Submit product data for all lighting controls.
d. Documentation or attestation that the building meets the DarkSky Luminaires Program, Version 3.0.	Comment by Customization Instructions: Retain if 3.3, DarkSky selected for points. If DarkSky is selected, delete all other items under Criterion 3.3.
e. Documentation or attestation that the building meets the Florida Fish and Wildlife Conservation Commission (FWC) Guidelines.	Comment by Customization Instructions: Retain if 3.3, FWC selected for points. If FWC is selected, delete all other items under Criterion 3.3.
6. Criterion 3.4: Surface Stormwater Management	Comment by Customization Instructions: Retain if project is:
New construction
Substantial or Moderate Rehab, and land disturbed is greater than 5,000 ft2.
Claiming optional points under Criterion 3.4.	Comment by Customization Instructions: NYC Overlay: Delete this criterion.
a. Submit as-built site plan or photo documentation showing surface stormwater management features installed in accordance with the surface stormwater management design, or other documentation as required by project team.
7. Criterion 3.5: Outdoor Water Use: Efficient Irrigation	Comment by Customization Instructions: Delete if project does not include irrigation or landscaping.
a. Product data for automated irrigation controllers.
b. Submit product data (including cut sheets, control sequence and instructions, operations and maintenance data, and warranty information) for drip irrigation system.	Comment by Customization Instructions: Delete if drip irrigation is not included in project design.
c. Submit product data (including cut sheets, control sequence and instructions, operations and maintenance data, and warranty information) for smart irrigation controllers programmed and commissioned by a Certified Irrigation Auditor.	Comment by Customization Instructions: Delete if smart controllers are not included in project design.
8. Criterion 3.6: Outdoor Water Use: Alternative Sources	Comment by Customization Instructions: Delete if project is not claiming optional points under Criterion 3.6.
a. Product data (cut sheets, control sequence and instructions, operations and maintenance data, and warranty information) for all system components related to water reuse for irrigation including storage tank(s), plumbing valves and controls, and other associated equipment.
b. Documentation that the irrigation system is installed according to the design of a professional certified by the American Rainwater Catchment Systems Association.	Comment by Customization Instructions: Delete if project is not using rainwater as an alternative water source. (Criterion 3.6, Option 2)
9. Criterion 3.7: Traffic Safety and Mobility
a. For all selected strategies, provide photos or other documentation showing installed measures:
i. Curbless Street: If paving patterns are used to delineate pedestrian-only space, submit photo documentation showing installed pattern or texture differentiation between pedestrian and vehicular space.	Comment by Customization Instructions: Retain if Curbless Street is selected to fulfill mandatory requirements (New Construction/Substantial Rehab) or earn optional points (Moderate Rehab).
ii. Roadway-Adjacent Sidewalk: Product data (including cut sheets, control sequence and instructions, operations and maintenance data, and warranty information) for crossing signals.	Comment by Customization Instructions: Retain if Roadway-Adjacent Sidewalk is selected to fulfill mandatory requirements (New Construction/Substantial Rehab) or earn optional points (Moderate Rehab).
10. Criterion 3.8: Heat-Island Management	Comment by Customization Instructions: Retain if project is:
New construction 
Substantial rehab
Moderate rehab using Criterion 3.8 for optional points. 
a. Product data for roofing materials showing three-year-aged solar reflectance index (SRI).	Comment by Customization Instructions: Retain if Criterion 3.8, Option 1: Roofing materials is used.
b. Submit product data indicating solar reflectance of paving materials and/or product data showing paving system classification.	Comment by Customization Instructions: Retain if Criterion 3.8, Option 2: Paved surfaces is used.
11. Criterion 3.9: Resilient Site Design: Wind
a. Submit product data as required for FORTIFIED Multifamily.	Comment by Customization Instructions: Retain a. and b. if Criterion 3.9, Option 1: FORTIFIED designation is selected to earn optional points.
b. Proof of FORTIFIED certification.
c. Submit documentation showing compliance with selected HUD “One-Pagers”:	Comment by Customization Instructions: Retain if Criterion 3.9, Option 2: HUD one-pagers for wind is selected to earn optional points.

Retain only the specifications below which are applicable based on selected HUD strategies.
i. Openings/Shutters
a. Photos of entry doors shows they are installed to swing out.
b. Product data for all exterior door assemblies show pressure and impact rating or protection by a system that is rated for the exposure category, design wind speed, and door size.
ii. Roof Deck and Underlayment 
a. Product data for plywood or OSB decking indicating thickness.
b. Product data for roof decking nails.
c. Product data for roof deck flashing tape, felt, and button-cap nails.
d. Product data for self-adhered membrane for roofing underlayment.
e. Product data for metal cap nails used to fasten underlayment.
f. Product data for plastic cap nails used to fasten underlayment.
iii. High-Wind Roof Covering: Product showing wind rating of asphalt shingles or other roof coverings.
iv. Continuous Load Path
a. Product data for wood structural panels used for gable end sheathing.
b. Product data for fastener used to attach roof framing members to wall top plates.
c. Representative photos of blocking installed between top plates and roof sheathing.
d. Product data for sill plate anchor bolts and washers.
v. Garage Doors: Documentation for the garage door assembly (door and all associated hardware and components) showing wind pressure rating (and impact rating, if doors include glazing), OR product showing wind and impact rating of shutter/screen installed to protect the garage door.
vi. Wall System
a. Product data for vinyl siding.
b. Product data for fiber cement cladding and attachments showing wind and pressure ratings.
vii. Soffit: Product data for soffit.
viii. Chimney: Photo documentation showing chimney height or installation in accordance with the design of a certified engineer.
ix. Roof-mounted equipment: 
a. Product data for solar PV showing rating for wind and snow/hail rating.
b. Photo of ground-mounted HVAC systems.
c. Photo of ground-mounted PV panels.
d. Photo of ground-mounted deck.
12. Criterion 3.10: Resilient Site Design: Flood	Comment by Customization Instructions: NYC Overlay: All projects located on flood-prone sites as defined by the HPD Design Guidelines are required to comply with this Criterion.
a. Option 1: ASCE 24-24 Compliance 	Comment by Customization Instructions: Retain if Criterion 3.10, Option 1: ASCE 24-24 compliance is used.
i. Product data, as required by project team, showing that installed products meet applicable standards in ASCE 24-24.
b. Option 2: HUD One-Pagers for Wind 	Comment by Customization Instructions: Retain if Criterion 3.10, Option 2: HUD one-pagers for water is selected to earn optional points.

Retain only the specifications below which are applicable based on selected HUD strategies (Connectors & Fasteners is always required if Option 2 is chosen).
i. Product data for connectors and fasteners.
ii. Wall Assembly: 
a. Product data for gypsum board and associated fasteners.
b. Representative photos of borate treatment on framing
c. Product data for closed cell spray foam wall insulation.
d. Representative photos showing locations of installed insulation.
e. Product data for cladding and trim.
f. Representative photos of furring on exterior walls
g. Product data for wall sheathing
iii. Freeboard Elevation: Documentation showing final installed elevation of lowest floor, for Coastal Zone A. For Coastal Zone V: Documentation showing final installed elevation of the bottom of the lowest horizontal structural member. Possible documentation could include a site survey, elevation certification, or requiring coordination with a licensed surveyor.
c. Option 3: Floodproofing of Critical Services	Comment by Customization Instructions: Retain if Criterion 3.10, Option 3: Floodproofing of critical services is selected to earn optional points.
i. Product data for floodproofing barriers (including windows, doors, impermeable panels, flood shields, as applicable).
ii. Representative photos of HVAC equipment being elevated, as applicable.
13. Criterion 3.11: Resilient Site Design: Wildfire	Comment by Customization Instructions: Retain if Criterion 3.11 is selected to earn optional points:
 a. through c. apply for all projects
 d. through h. apply only for projects earning 12 points
a. Product data for roof covering materials. 
b. Product data for soffits.
c. Product data for windows.
d. Product data for vegetation planted within 5-30 feet of each building (ignition zone 1).
e. Product data for landscaping ground cover used within 5-30 feet of each building (ignition zone 1).
f. Product data for metal mesh covering vents indicating opening size.
g. Product data for siding and cladding materials.
h. Product data for materials used in deck and balcony construction.
Water
14. Criterion 4.1: Water-Conserving Fixtures and 4.2 Advanced Water Conservation	Comment by Customization Instructions: NYC Overlay: All projects are required to comply with Criterion 4.2.
a. Product data documenting consumption metrics for all installed fixtures and equipment (new and existing):
- Toilets: flush rate in gallons per flush (gpf)
- Showerheads (per compartment): flow rate in gallons per minute (gpm) 
- Kitchen and lavatory faucets: flow rate in gallons per minute (gpm)
- Clothes washer: integrated water factor (IWF)
- Dishwasher: gallons per cycle (gpc)
b. WaterSense certification documentation for all newly installed toilets, showerheads, and lavatory faucets.
c. Documentation of service pressure and product data for pressure regulator (if applicable).	Comment by Customization Instructions: Delete if multifamily more than 3 stories.
d. Submit documentation of whole-home water certification.	Comment by Customization Instructions: Retain if Criterion 4.2, Option 2: Whole-home certification is selected to earn optional points. 

If Option 2 is selected, delete items a., b., and c. in this section.
15. Criterion 4.3: Water Quality
a. If lead service lines must be replaced:	Comment by Customization Instructions: Retain if project is:
Substantial Rehab constructed before 1986
Substantial Rehab constructed in 1986 or later, and this requirement is selected for optional points.
Moderate Rehab, and this requirements is selected for optional points.
i. Submit product data for replacement water service lines and fittings.
ii. Inspection reports and/or photographs documenting preliminary conditions and all completed water line replacements.
b. If water testing and remediation is performed: 	Comment by Customization Instructions: Retain if project selects this requirement to earn optional points. 

Retain only the items below which are selected for optional points and applicable based on test results.
i. All water quality test results from representative fixtures.
ii. If lead remediation is required (and test results show < 5ppb):
a. Product data for installed dwelling unit faucet water filters.
iii. If lead remediation is required (and test results show >= 5 ppb):
a. Product data for replacement dwelling unit fixtures.
iv. If nitrate remediation is required:
a. Specifications for installed reverse-osmosis or ion-exchange water treatment system.
v. If any test results trigger application of remediation per local health department, provide remediation requirements
16. Criterion 4.4: Monitoring Water Consumption and Leaks	Comment by Customization Instructions: Retain if Criterion 4.4 is selected to earn optional points. If Criterion 4.4 is selected, item a. is always required.

For remaining items, retain only those which are selected for optional points. Option 2 is only available for rehab projects.
a. Pressure-loss test results and visual inspection report.
b. Option 1: Product data for installed water-monitoring and leak-detection system.
c. Option 2:  
i. Pre-rehabilitation leak assessment report with description of test method used, test results, test locations, location and severity of observed leaks, photo documentation, corrective-action log with status of each issue (fixed, deferred, or in scope), baseline consumption chart/summary, and audit checklist.
ii. Construction-Phase Leak Monitoring and Response Log, including a documentation of temporary leak monitoring activities, dates of weekly walk-down inspections, locations of new leaks identified during construction and selective demolition, corrective actions implemented, and status of resolution. Include photographs of significant leak events and moisture damage.	Comment by Customization Instructions: Retain if domestic hot water remains active during construction.
d. Option 3: Product data for all installed water meters and a meter schedule indicating location, metered end use, and communications method. Submit results from commissioning of water metering system, as required by project team.
17. Criterion 4.5: Efficient Plumbing Layout and Design	Comment by Customization Instructions: Retain if Criterion 4.5 is selected for optional points. If Criterion 4.5 is selected, item a. is always required. 

For remaining items, retain only those which are selected for optional points. 	Comment by Customization Instructions: NYC Overlay: New Construction projects are required to comply with this Criterion.
a. If in-dwelling recirculation pump is installed, submit product data for recirculation pump controls and control sequence describing system operation.
b. Option 2: Documentation of WaterSense certification.
c. Option 3, Strategy B:
i. Product data for dwelling unit water heaters.
ii. WaterSense certification for all dwelling unit showerheads, bath faucets, and aerators.
iii. Product data for recirculating central hot water distribution system pipe insulation documenting insulation thickness and R-value.
18. Criterion 4.6: Indoor Water Efficiency: Nonpotable Water Reuse	Comment by Customization Instructions: Retain if Criterion 4.6 is selected for optional points.
a. Documentation including product data, schematics, and schedules for greywater sources, end uses, piping, backflow preventers, storage tank(s), and cross connection prevention measures. 
19. Criterion 4.7: Access to Potable Water During Emergencies	Comment by Customization Instructions: Retain if Criterion 4.7 is selected for optional points. Retain only the option selected by the project team.	Comment by Customization Instructions: NYC Overlay: Delete this Criterion.
a. Option 1: Documentation indicating potable water source and location, ADA accessibility, and elevation. 
b. Option 2: Documentation indicating on-site potable water storage tank capacity, location, ADA accessibility, elevation, and manufacturer maintenance instructions. 
c. Option 3: Product data for on-site well pumping equipment including power source (if required for pump operation) and identification of water access points during power outages.
Energy   
20. Criterion 5.2a: Building Performance	Comment by Customization Instructions: Retain if project is:
New Construction
NOT using Criterion 5.3, Option 2
a. ENERGY STAR Multifamily New Construction certificate for every multifamily dwelling unit.
21. Criterion 5.2b: Building Performance	Comment by Customization Instructions: Retain if project is:
Substantial Rehab
Moderate Rehab
NOT using Criterion 5.3, Option 2
Retain only the option selected by the project team.
a. Option 1: Energy Rating Index: Submit ERI energy rating certificates for every dwelling unit demonstrating an ERI score of  [80 / 90] or less, excluding on-site power generation.	Comment by Customization Instructions: Select ERI target based on project type:
Moderate rehab pre-1980: 90
Substantial rehab or moderate rehab post-1980: 80
b. Option 2: ASHRAE 90.1: Energy model report demonstrating project energy performance equivalent to or better than ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016, excluding on-site power generation.
c. Option 2: Project in California: Energy model report demonstrating project energy performance equivalent to or better than the version of Title 24 under which the project is permitted.
d. Projects using Energy Outreach Colorado Program: Documentation that project meets requirements of Energy Outreach Colorado.
e. Completed ENERGY STAR Multifamily New Construction HVAC Functional Testing Checklist Version 1.1 for 100% of existing HVAC systems.
f. Completed ENERGY STAR Multifamily New Construction HVAC Functional Testing Checklist Version 1.1 for new HVAC systems, following sampling guidance provided by ENERGY STAR.
g. Heating and cooling load calculations and equipment selection.
h. Product information for any newly installed thermal insulation showing R values.
i. Product information for all permanently installed lighting.
j. ENERGY STAR certification for all installed clothes washers, dishwashers, and refrigerators.
k. NYC Overlay: Product data as required by the New York City Prescriptive Pathway for Tenant in Place Rehabs.	Comment by Customization Instructions: NYC Overlay: Delete if NYC Overlay not used.
22. Criterion 5.3: Advanced Building Performance	Comment by Customization Instructions: Retain if Criterion 5.3 is selected for points. Retain only the option selected by the project team.
a. Option 1: Performance Above Mandatory Requirement (New Construction): ENERGY STAR Multifamily New Construction certificate for every dwelling unit showing performance at least 5 points more efficient than the program's ERI Target Score or at least 5% more efficient than the program's ASHRAE target.
b. Option 1: Performance Above Mandatory Requirement (Rehabilitation, ERI Path): ERI energy rating certificate for every dwelling unit demonstrating an ERI score of [75 / 85] or less, excluding on-site power generation.	Comment by Customization Instructions: Select ERI target based on project type:
Substantial rehab with no historic designation: 75
Moderate rehab or substantial rehab with historic designation: 85
c. Option 1: Performance Above Mandatory Requirement (Rehabilitation, ASHRAE Path): Energy model report demonstrating project energy performance at least 5% better than ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016, excluding on-site power generation.
d. Option 1: Performance Above Mandatory Requirement (Rehabilitation, Title 24 Path): Energy model report demonstrating project energy performance at least 5% better than the version of Title 24 under which the project is permitted.
e. Option 2: Advanced Building Certification (DOE Efficient New Homes): DOE Efficient New Homes certificate for every dwelling unit for the program version applicable based on project type and permit date.
f. Option 2: Advanced Building Certification (ENERGY STAR NextGen): ENERGY STAR NextGen certificate for every dwelling unit.
g. Option 2: Advanced Building Certification (Passive House International): Proof of certification under Passive House International Classic, Plus, Premium, LEB, or EnerPHit.
h. Option 2: Advanced Building Certification (Phius): Proof of certification under Phius CORE, ZERO, or REVIVE.
i. Option 3: Deep Energy Retrofit (Rehabilitation, ERI Path): Submit ERI energy rating certificate for every dwelling unit demonstrating an ERI score of [65 / 75] or less, excluding on-site power generation.	Comment by Customization Instructions: Select ERI target based on project type:
Substantial rehabs: 65
Moderate rehab: 75
j. Option 3: Deep Energy Retrofit (Rehabilitation, ASHRAE Path): Energy model report demonstrating project energy performance at least [10% / 15%] better than ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016, excluding on-site power generation.	Comment by Customization Instructions: Select target based on project type:
Substantial rehabs: 15%
Moderate rehabs: 10%
k. Option 3: Deep Energy Retrofit (Rehabilitation, Title 24 Path): Energy model report demonstrating project energy performance at least [10% / 15%] better than ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016, excluding on-site power generation.	Comment by Customization Instructions: Select target based on project type:
Substantial rehabs: 15%
Moderate rehabs: 10%
23. Criterion 5.4: All-Electric and Electric-Ready Design
a. Product data for cooking equipment.	Comment by Customization Instructions: Retain if project is:
New Construction
Rehab, and Criterion 5.4b is selected to earn optional points	Comment by Customization Instructions: NYC Overlay: Delete a. if selecting to use the Rehab option to electrify space heating only.
Option 1: Electric Ready
b. Photo documentation of electric-ready features for space heating:	Comment by Customization Instructions: Retain if project is:
New construction, including gas heating
Rehab, including gas heating, and Criterion 5.4b is selected to earn optional points.
i. No obstructions exist between branch circuit and gas space heating appliances in dwelling units and that the circuit is not used for other appliances.
ii. Space in the electric panel next to the space heating breaker labeled "240 Ready."
iii. Both ends of unused electric space heater wiring are labeled.
c. Photo documentation of electric-ready features for water heating:	Comment by Customization Instructions: Retain if project is:
New construction, including gas water heating
Rehab, including gas water heating, and Criterion 5.4b is selected to earn optional points.
i. No obstructions exist between branch circuit and gas water heating appliances in dwelling units and that the circuit is not used for other appliances.
ii. Space in the electric panel next to the water heating breaker labeled "240 Ready."
iii. Both ends of unused electric water heater wiring labeled.
iv. 3x3 feet of clear floor space with a clearance height of at least 6 feet.	Comment by Customization Instructions: Retain if project is:
New construction, including gas storage water heating 
Rehab, including gas storage water heating, and Criterion 5.4b is selected to earn optional points
v. Floor drain near the 3x3 foot space.
Option 2: All-Electric
d. Product data for all space heating, water heating, and clothes dryer equipment.	Comment by Customization Instructions: Retain if project is:
New construction, and Criterion 5.4a is selected to earn optional points. 
Rehab, and Criterion 5.4b, Option 2: All-electric property is selected to earn optional points.
If this option is selected, delete b. and c., above.
NYC Overlay	Comment by Customization Instructions: NYC Overlay: This option is available to NYC overlay rehab projects only.
e. Product data for all space heating and cooling equipment.
24. Criterion 5.5: Peak Demand Control	Comment by Customization Instructions: Retain if Criterion 5.5, Option 1: Hot-water thermal storage and control is selected to earn optional points.
Option 1: Hot-Water Thermal Storage and Control: 
a. Product data for hot water system that identifies capacity, storage, and control capabilities.
b. Specifications or control interface and operating instructions for hot water thermal storage and control.
25. Criterion 5.6: Backup Power	Comment by Customization Instructions: Retain if Criterion 5.6 is selected to earn optional points. Retain only the specs below which apply based on the Option selected by the project team.	Comment by Customization Instructions: NYC Overlay: This Criterion is required for NYC Overlay projects. An additional option is available to comply - “Shelter in Place Area” (see Execution).
a. Documentation of transferring / islanding controls to enable backup power during grid outages and critical loads served 
b. Option 1: Islandable PV + Battery Storage: Product data for islandable solar photovoltaics and battery storage.
c. Option 2: Off-peak Battery Storage: Product data for battery energy storage system.
d. Option 3: Generator: Product data for backup generator(s) and fuel storage equipment.
26. Criterion 5.7: Renewable Energy	Comment by Customization Instructions: Retain if Criterion 5.7, Option 1 is selected to earn optional points. Retain only the Strategy selected by the project team. 
a. Strategies A, B, and D: Product data for installed PV, including system capacity and area of installed array.
b. Strategy C: Geothermal system data including system capacity
27. Criterion 5.8: Electric Vehicle Charging 	Comment by Customization Instructions: Retain if project is:
New Construction or Substantial Rehab and project includes parking.
Moderate Rehabs, and Criterion 5.8 is selected to earn optional points.
Retain only specification for EVSE, Capable, and Ready as applicable based on options selected by project team.
a. Documentation showing locations of all installed EVSE, EV-capable, and EV-ready spaces and associated circuits.
b. Product data for Level 2 electric vehicle supply equipment (EVSE) and photos of installed EVSE, if present.
c. Photos of any installed EV-capable or EV-ready infrastructure, if present.
d. Product data for Automatic Load Management System (ALMS), if used, including delivered capacity and programming information.
28. Criterion 5.9: Passive Survivability	Comment by Customization Instructions: Retain if Criterion 5.9 is selected to earn optional points. Retain specs for strategies that are selected by project team.
a. Option 1 - Natural Ventilation: Product data for dwelling unit windows.
b. Option 1 - Shading: Product data, locations, and installed photos of shading equipment installed in south-facing windows, if present.
Materials
29. Criterion 6.2: Reduction of Materials and Waste	Comment by Customization Instructions: Retain if Criterion 6.2 is selected to earn optional points. Retain only strategies selected by project team.
a. Strategy E: Product data for salvaged materials for [Flooring / Ceilings / Doors / Glazing / Millwork / Lighting / Plumbing Fixture / Insulation / Landscape Paving / Furniture] including quantity used and original source.	Comment by Customization Instructions: Product category selected by project team.
b. Strategy F: Documentation of a salvage assessment completed prior to demolition, identifying building materials, soils, and landscaping to be removed and plans to divert at least 35% from landfill.
c. Strategy I: Document end-of-use guidance for five product categories, identifying products, locations in the building, installed quantities, anticipated life spans, and recommended actions to salvage them or recover them for recycling. Include information for specific organizations or businesses that will assist with end of use.
d. Strategy J: Product data for products with extended producer responsibility programs (e.g., take-back programs). Provide a list of product categories, products, installed quantities, and program information.
e. Strategy K: Provide a list of assemblies in the building that are designed for disassembly. Include their locations in the building, the quantity of recoverable materials, and guidance or diagrams on the disassembly method.
f. Strategy L: Document guidance on disassembly methods for installed modular construction elements.
30. Criterion 6.3: Reduction of Lead Hazards in Pre-1978 Buildings	Comment by Customization Instructions: Retain if project is a substantial rehab in a pre-1978 building, and Option 1 is selected to satisfy Criterion 6.3.
a. Submit credentials complying with EPA’s Renovation, Repair, and Painting Regulation (RRP) (40 CFR 745) requirements.
31. Criterion 6.4: Advanced Material Selection	Comment by Customization Instructions: Delete any product-specific specs that are not selected for points by the project team. Optional products are indicated with brackets.
a. Submit VOC level in grams per liter for all adhesives and sealants applied inside the air barrier.
b. Submit verification that adhesives and sealants applied inside the air barrier meet the CDPH Standard Method for the school or residential scenario (required for 80% by volume).
c. Cladding: Product data for exterior wall cladding.
d. Concrete: Environmental product declarations (EPDs) for 90% of newly installed concrete, including GWP.
e. Flooring
i. Option 1: Best-in-class: Product data for flooring, including any FSC certifications, as applicable.
ii. Option 2: Minimum Standard: Product data for flooring, including verification that VOC emissions meet requirements of CDPH Standard Method for school or residential scenarios.
For additional points:
a. Product data for flooring adhesives, coating, and sealants (including pre-applied and site-applied).
f. Gypsum Wallboard: Product data for 60% of newly installed interior gypsum wallboard, including documentation of compliance with CDPH Standard Method emission requirements.
g. Product data for newly installed insulation.
h. Submit VOC level in grams per liter for all interior paints, coatings, and primers.
i. Submit verification for any interior paints, coatings, and primers that meet the CDPH Standard Method for the school or residential scenario.
j. Steel
i. Option 1: Best-in-class: Product data for steel, including documentation of production method and percentage of recycled content.
ii. Option 2: Intermediate: Product data for 75% of steel deck, cold-formed steel framing, and structural steel, including documentation of GWP.
k. Product data for wall coverings.
l. Product data for all hardwood plywood, particleboard, medium-density fiberboard (MDF), and these materials within other products (e.g., cabinets and doors). Data must show level of formaldehyde emissions from these products.
For additional points:
i. Include FSC certifications for at least 50% of these products.
m. Wood, noncomposite: FSC certifications for 50% of installed non-composite wood.
32. Criterion 6.5: Recycling Storage	Comment by Customization Instructions: Retain if Criterion 6.5 is used to earn optional points and municipal recycling is present.	Comment by Customization Instructions: NYC Overlay: Criterion 6.5 is mandatory.
a. Photos documenting recycling storage equipment and signage.
Healthy Living Environment
33. Criterion 7.1: Clean Air - Radon Testing and Mitigation
a. New Construction	Comment by Customization Instructions: Retain if project is New Construction, Radon Zone 1. 
i. Photographs of installed radon-resistant construction features: below slab, vent pipe, and adjacent electrical outlet.
ii. Submit one of the following, or other documentation as indicated by project team, to show compliance with Section 5.2 of ANSI/ASHRAE Standard 62.1-2022:
1) TAB report or field measurements documenting pressure differential between attached parking garages and immediately adjacent occupiable spaces.
2) As-built plans and/or installed photographs showing a vestibule that provides an airlock between the garage and occupiable space.
3) Documentation that the project limits migration of air from the attached parking garage into the adjacent occupiable spaces of the building in a manner acceptable to the authority having jurisdiction (AHJ).	Comment by Customization Instructions: Retain if building has a garage attached to a foundation system and chooses to comply with Standard 62.2 in lieu of meeting passive radon-resistant features. If this option is selected, delete i. above.
b. Substantial Rehab 	Comment by Customization Instructions: Retain if project is a substantial rehab multifamily building located in Radon Zone 1.
i. Pre-construction test results (conducted by a radon professional in accordance with ANSI-AARST MA-MFLB-2023). If test results exceed 4 pCi/L (picocuries per liter), submit photographs of installed radon-reduction measures outlined in ANSI-AARST SGM-MFLB-2023.
ii. Post-Construction test results (conducted by a radon professional in accordance with ANSI-AARST MA-MFLB-2023). If test results exceed 4 pCi/L (picocuries per liter) and exceed pre-construction test results, submit photographs of installed radon-reduction measures outlined in ANSI-AARST
34. Criterion 7.2: Clean Air - Combustion Equipment	Comment by Customization Instructions: Retain if project includes any combustion equipment, unless combustion equipment is located only in detached utility buildings or non-enclosed spaces.  
a. Product data for carbon monoxide alarms.
b. Product data for any new combustion appliances, water heating, and space heating equipment, including venting capabilities.
c. Report results of combustion safety testing prior to and after the retrofit for central systems and for 10% of individual dwelling-unit systems.	Comment by Customization Instructions: Retain if project is a substantial or moderate rehab.
35. Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management
a. Photos documenting idling signage in parking and drop-off areas.
b. Product data for carbon monoxide alarms.	Comment by Customization Instructions: Delete if project:
Does not have a parking garage
Has a mechanically vented garage
Only has open parking structures
36. Criterion 7.5: Clean Air – Ventilation	Comment by Customization Instructions: Retain if project is:
New construction 
Substantial rehab
Moderate rehab, and Criterion 7.5 is selected to earn optional points. For Moderate rehabs, retain only the options selected to earn points by the project team.
a. Product data for in-unit kitchen mechanical exhaust system.
b. If no combustion-fueled appliances are located within the dwelling unit, provide product data for a heat- or energy-recovery ventilator or a ceiling- or wall-mounted fan.	Comment by Customization Instructions: Retain if Criterion 5.3, Option 2: Advanced building certification is selected to earn optional points.
c. Product data for bathroom mechanical exhaust system. Include proof of ENERGY STAR  certification for fans serving individual bathrooms.
d. Product data for whole-house mechanical ventilation system.
e. Product data for a mechanical ventilation system serving all hallways, stairwells, and common/amenity spaces.	Comment by Customization Instructions: Retain if project is four stories or more.
f. Product data for real-time data logging equipment for systems delivering 2,000 CFM or more of outdoor air.
37. Criterion 7.6: Clean Air - Indoor Air Filtration	Comment by Customization Instructions: Retain if new central HVAC system is installed.
a. Product data for HVAC system filter.
38. Criterion 7.7: Clean Air - Enhanced IAQ	Comment by Customization Instructions: Retain if Criterion 7.7, Option 2: Indoor AirPlus is selected to earn optional points.	Comment by Customization Instructions: NYC Overlay: Criterion 7.7, Option 1 or 2 is required.
a. Certificates showing that each dwelling unit is certified under the EPA Indoor AirPlus program.
39. Criterion 7.8: Moisture – Dehumidification	Comment by Customization Instructions: Retain if project is:
Located in CZ 1A, 2A, 3A, or 4A, and has selected Criterion 5.3 to earn optional points. 
Located in any other CZ, and selected Criterion 7.8 to earn optional points.
Retain only the Option selected by the project team.
a. Option 1: Dedicated Dehumidification System: Product data for supplemental dehumidification equipment.
b. Option 2: Dehumidification Readiness: Photos documenting dehumidification readiness measures, including dedicated space, drains, and electrical hook-ups.
c. Option 3: ERV or HRV	Comment by Customization Instructions: NYC Overlay: All projects following Criterion 5.3 are required to comply with Criterion 7.8 by meeting Option 3: ERV or HRV.
i. Product data for energy-recovery ventilator (ERV) or heat-recovery ventilator (HRV).
ii.  Written statement from mechanical engineer attesting that buildings and systems have been designed to ensure that year-round interior relative humidity will not exceed 50% in the winter and 60% in the summer.
iii. Narrative summarizing H/ERV control strategies used to manage year-round interior relative humidity.
iv. Drawings of H/ERV system(s) showing relative humidity monitors in return-air ducts at the H/ERV to monitor relative humidity.
v. Condensation evaluation for window-to-wall connections and at any non-thermally-broken metal penetrations through the exterior envelope, or Passive House thermal bridge modeling report (if pursuing Passive House certification).
40. Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	Comment by Customization Instructions: Retain if project is new construction.
a. Product data for polyethylene sheeting vapor retarder.
41. Criterion 7.9b: Managing Moisture in the Building Envelope – Rehabilitation	Comment by Customization Instructions: Retain if project is substantial or moderate rehab.
a. List of repairs and remediations that will be included in the scope of work based on the property assessment, indicating any that must occur before the rehab begins.
42. Criterion 7.10 Managing Moisture: Bath, Kitchen, and Laundry Assemblies	Comment by Customization Instructions: Retain if project is:
New construction
Substantial rehab
Moderate rehab, and bathroom is in scope.
a. Product documentation for all cement board or fiber-cement board installed behind tub and shower enclosures.
43. Criterion 7.11: Reducing Allergens and Disease Vectors - Integrated Pest Management
a. Submit product data for low-VOC caulking or other low-hazard sealing methods including window screens, door sweeps, escutcheon plates, and rodent- and corrosion-proof screens for openings greater than ¼ inch.
44. Criterion: 7.12a Sensory and Rest Friendly: Noise Reduction, New Construction	Comment by Customization Instructions: Retain if project is new construction and Criterion 7.12a is selected to earn optional points. Retain only the Option(s) selected by the project team.
a. Option 1: Outdoor Noise Abatement 
i. Documentation showing composite Outdoor-Indoor Transmission Class (OITC) rating for exterior walls.
ii. Documentation showing Outdoor-Indoor Transmission Class (OITC) rating for windows.
b. Option 2: Indoor Sources of Noise
i. Documentation showing Sound Transmission Class (STC) or Apparent Sound Transmission Class (ASTC) rating for separation walls.
ii. Documentation showing Impact Insulation Class (IIC) or Apparent Impact Insulation Class (AIIC) rating for floor and ceiling assemblies between dwelling units.
45. Criterion 7.12b: Sensory and Rest Friendly: Noise Reduction, Rehabilitation	Comment by Customization Instructions: Retain if project is substantial or moderate rehab and Criterion 7.12b is selected to earn optional points. Retain only the Option(s) selected by the project team.
a. Option 1: Documentation of noise assessment and site-specific noise-abatement plan in accordance with HUD regulation 24 CFR Part 51, Subpart B.
b. Option 2 – Minimal or Advanced:
i. Documentation showing composite Outdoor-Indoor Transmission Class (OITC) rating for exterior walls.
ii. Documentation showing Outdoor-Indoor Transmission Class (OITC) rating for windows.
c. Option 3: Interior Sources of Noise in Bedrooms: Documentation showing bedroom party walls meet requirements of ICC G2-2010 Guideline for Acoustics and verification of Grade achieved.
46. Criterion 7.13: Personal and Social Safety	Comment by Customization Instructions: Retain if project is:
New Construction 
Substantial rehab
Retain only the strategies selected by the project team.
a. Strategy B: Product data for “peephole” door viewers or dwelling-unit entry doors that include windows.
b. Strategy H: Product data for drinking fountain or hydration station.
c. Strategy I (more than 12 units): Product data for lockable package storage or lockers.
d. Strategy I (fewer than 12 units): Product data for lockable mailboxes.
47. Criterion 7.14: Social Connection and Accessibility - Design for All Ages/Abilities	Comment by Customization Instructions: Retain only strategies selected by project team.
a. Strategy A: Photos of signage for wayfinding.
b. Strategy B: Photos of interior floor finishes.
c. Strategy D: Product data for furniture in common spaces.
d. Strategy F: Photos of features for universal accessibility in common area bathrooms.
e. Strategy H: Product data for floor finishes used in common spaces, hallways, entryways, and outdoor pathways.
f. Strategy I: Product data for bathroom grab bars and towel bars.
g. Strategy J: Product data for thermostatic or anti-scald faucets.
h. Strategy K: Photos showing thresholds for interior and exterior doors.
i. Strategy L: 
i. Product data for dwelling unit door handles.
ii. Product data for drawer and cabinet hardware.
iii. Product data for faucets.
iv. Product data for light switches.
j. Strategy P: Photo of storage space for mobility equipment (wheelchairs, walkers, electric scooters, strollers).
48. Criterion 7.15: Access to Nature and Biophilic Design	Comment by Customization Instructions: Retain if Criterion 7.15 is selected to earn optional points. Retain only specs selected by project team for points.
a. Product data for tunable circadian lighting systems.
b. Product data for vegetation.
c. Product data for flowering plants, bird baths, pollinator houses, bat houses, or perches, as applicable.
d. Photos of installed water features (fountains, rain chains, bioswales, as applicable).
49. Criterion 7.16 Healing-Centered and Culturally Responsive Design
a. Photos of artwork installed in shared indoor or outdoor space.	Comment by Customization Instructions: Retain if Criterion 7.16, Community-generated art, is selected to earn optional points.
b. Photos of three installed design and naming elements selected by community members.	Comment by Customization Instructions: Retain if Criterion 7.16, Storytelling through space, is selected to earn optional points.
50. Criterion 7.17 Active Design: Promoting Physical Activity	Comment by Customization Instructions: Retain if Criterion 7.17 is selected to earn optional points. Retain only Options/specs selected by project team for points.
a. Option 1: Product data for finishes in stairways and building corridors.
b. Glazing: Product data for glazing used at stair doors (glazing within doors or a sidelite).
c. Door Holds: Product data for magnetic door holds.
d. Option 2: Product data for adult exercise and/or children's play equipment.
Operations, Maintenance, and Resident Engagement
51. Criterion 8.1: Building Operations and Maintenance Manual and Plan
a. Submit a manual with thorough building operations and maintenance guidance and a complementary plan, including all of the following components:
b. Floor plans specifically highlighting the location of mechanical, electrical, fuel, and water-system turnoffs.
c. A list of topics included in the emergency management manual and where this manual is available.
d. Green cleaning product specifications and cleaning schedules.
e. Operations and maintenance guidance for all mechanical, electrical and plumbing equipment and appliances for building-level equipment and dwelling-unit equipment, including HVAC and plumbing as-built information and specifications, maintenance schedules, and any established contracted services and service providers.
f. As-built lighting fixture and lamp schedules, specifications, and replacement guidance.
g. As-built landscaping and hardscaping plant lists, specifications, maintenance requirements and schedules, and any specific instructions for community gardens or growing spaces.
h. As-built specifications, maintenance requirements, and replacement schedules for paint and other finishes that require regular updates.
i. Specifications, maintenance schedules, and any established contracted services and service providers for backup power systems and any other specialized systems, e.g., solar photovoltaics, solar water heating, ground-source heating and cooling, cogeneration.
j. Name and purpose of each community-portal application for sharing information between building personnel and residents.
k. A copy of the property’s Zero Over Time plan (if the project is pursuing Criterion 5.1 Energy Planning) and guidance to refer to this plan for equipment replacement and capital planning.
l. Maintenance requirements for equipment installed in active recreation and play spaces or other site amenities.
m. Type and location of any supporting tools for staff and residents (magnets, short informational videos, QR code stickers).
52. Criterion 8.2: Emergency Management Manual
a. Submit information critical to an Emergency Management Manual related to operations such as infrastructure and building shutdown procedures, including appropriate steps for securing electrical and mechanical systems, on-site fuel sources, elevators, and the site perimeter, and potable water protection and supply.
53. Criterion 8.4: Walk-Throughs and Orientations to Property Operation
a. Documentation of a comprehensive walk-through for all residents and for all property managers and building operations staff.
54. Criterion 8.5: Energy and Water Data Collection and Monitoring	Comment by Customization Instructions: Delete if all units are owner-occupied.	Comment by Customization Instructions: NYC Overlay: Two additional options are available under this Criterion for projects receiving HPD subsidy. See NYC Overlay checklist for details.
a. Submit a screenshot of the project's dashboard in the benchmarking platform used to track and monitor energy and water data. If possible, ensure the screenshot includes the project name and physical building address.
[bookmark: _Toc233209875]Part 2 – Products
2.1  Product Requirements
1. Site Design
1. Criterion 3.2 Site Design for Ecosystem Services	
a. All landscape plantings, including trees, shrubs, and herbaceous plants, must be native or climate-appropriate (adapted) to the region.
b. All landscape plantings must be appropriate to the site’s soil and microclimate, and none should be invasive or non-adapted plant species.  
2. Criterion 3.3 Exterior Lighting	Comment by Customization Instructions: Delete Criterion 3.3 if scope does not include exterior lighting.
All permanently installed exterior lighting fixtures, with the exception of emergency lighting, must meet the following requirements or local requirements—whichever is more stringent.
a. All exterior lighting fixtures comply with DarkSky Luminaires Program Version 3.0.	Comment by Customization Instructions: Retain if 3.3, DarkSky selected for points. If DarkSky is selected, delete all other items under Criterion 3.3.
b. All exterior lighting fixtures comply with Florida Fish and Wildlife Conservation Commission (FWC) Guidelines.	Comment by Customization Instructions: Retain if 3.3, FWC selected for points. If FWC is selected, delete all other items under Criterion 3.3.
c. All exterior lighting fixtures do not have sag or drop lenses, side light panels, or uplight panels.
d. All exterior lighting has photo or motion sensors, integrative PV cells, or astronomic time-clock operation.
e. All exterior lighting are dimmable to 10% or less of their full light output.
f. All exterior lighting fixtures meet Backlight, Uplight, and Glare (BUG) ratings, U and G selected based on planned installation height and surrounding architectural features (see Execution):
i. B0 or B1; U0; G0
ii. B0 - B3; U0 or U1; G0 or G1
iii. B0 - B4; U0 - U2; G0 - G2
iv. B0 - B5; U0 - U3; G0 - G3
v. B0 - B5; U0 - U4; G0 - G4
3. Criterion 3.5 Outdoor Water Use: Efficient Irrigation		Comment by Customization Instructions: Delete if project does not include irrigation or landscaping.
a. Automated irrigation controllers are WaterSense certified and respond to weather data or soil moisture.
b. Smart irrigation controllers programmed and commissioned by a Certified Irrigation Auditor.	Comment by Customization Instructions: Delete if smart controllers are not included in project design.
4. Criterion 3.7 Traffic Safety and Mobility	
a. Child-safe gate or fence for recreation areas allows visibility between enclosed and unenclosed area.	Comment by Customization Instructions: Retain if Hazard-Adjacent Play Space is selected to fulfill mandatory requirements (New Construction/Substantial Rehab) or earn optional points (Moderate Rehab) under Criterion 3.7.
b. Auditory crossing signals programmed to ensure adequate crossing time per project team guidance.	Comment by Customization Instructions: Retain if Roadways is selected to fulfill mandatory requirements (New Construction/Substantial Rehab) or earn optional points (Moderate Rehab) under Criterion 3.7.
5. Criterion 3.8 Heat-Island Management		Comment by Customization Instructions: Retain if project is:
New construction 
Substantial rehab
Moderate rehab using Criterion 3.8 for optional points. 

Retain only the Option(s) and strategies selected by the project team.
Option 1: Roofing Materials
a. Climate Zones 1-3: Roofing materials have a minimum 64 SRI (roof slope £ 2:12) or 16 SRI (> 2:12). SRI rating is third-party certified.	Comment by Customization Instructions: Retain if Criterion 3.8, Option 1: Roofing materials is used.
b. Climate Zones 4-8: Roofing materials have a minimum 64 SRI (roof slope   2:12) or 32 SRI (> 2:12). SRI rating is third-party certified.
Option 2: Paved Surfaces 
c. Solar reflectance of paving materials at least 0.33.
d. Paving system classified as open-grid.
6. Criterion 3.9 Resilient Site Design: Wind		Comment by Customization Instructions: Retain if Criterion 3.9 is selected to earn optional points. Retain only the Option selected by the project team.
Option 1: FORTIFIED Designation
a. All products comply with FORTIFIED Multifamily requirements, including continuous roof covers, roof deck fasteners, flashing, drip-edge, coping, counter-flashing, wood nailers, gutters, roof deck materials, roof deck attachments, underlayments, ridge vents, skylights, roof-mounted equipment and lighting protection systems, and safety rails.
b. All wall systems, gable ends, windows, curtain walls, and doors meet impact-resistance and pressure ratings required by the FORTIFIED Multifamily requirements as applicable in hurricane-prone and high-wind-prone regions. 	Comment by Customization Instructions: Retain if FORTIFIED Multifamily Silver or Gold is selected.
c. For steep-sloped roofs: asphalt shingles rated Good or Excellent on the IBHS hail impact-resistant shingle ratings; clay and concrete roof tiles meet FM 4473 Class 4 impact rating; metal panels meet UL2218 Class 4 impact rating; all other roof covers meet either UL 2218 Class 4 rating or FM 4473 Class 4 rating.	Comment by Customization Instructions: Retain c. and d. if FORTIFIED Multifamily Hail Supplement is selected.
i. For low-sloped continuous roof covers: FM Approval Standard 4470 with a Class 1-SH or 1-VSH; OR UL 2218 Class 4.
Option 2: HUD One-Pagers for Wind	Comment by Customization Instructions: Retain only the specifications below which are applicable based on selected HUD strategies. At least two items from any single category must be selected in order to earn points for that category.
d. Openings/Shutters
i. Shutters are capable of protecting glazing from wind-borne debris.
ii. No windows are mulled.
iii. Exterior doors are outswing. 
iv. The door and windows, as an assembly, are rated for the design pressure.
v. The door assembly (door and all associated hardware and components) meet the design wind pressure for the site.
vi. All glazed openings (windows, patio doors, skylights, glass block, etc.) must be able to resist or be protected from wind-borne debris.
vii. All exterior door assemblies must be pressure and impact rated or protected by a system that is rated for the exposure category, design wind speed, door size, and door location on the building. Assembly includes door, door frame attachment to wood frame, and lock.
e. Roof Deck and Underlayment
i. Decking is plywood or OSB with a minimum width of 7/16 inches.
ii. Nailing for decking is 8d round head 2-1/2 inch, .131 ring shank nails.
iii. Sealing for deck seams is either:
a. 4-in wide ASTM D1970 compliant self-adhering polymer-modified bitume, OR
b. AAMA 711-13 Level 3 roof deck flashing tape
iv. Deck underlayment is #30 felt or equivalent synthetic underlayment.
v. Deck underlayment is #30 felt or equivalent synthetic underlayment.
vi. Deck underlayment is self-adhered (peel-and-stick) membrane meeting ASTM D1970 requirements.
vii. Fasteners for underlayment are 32-gauge metal cap nail with minimum 1 in. diameter—minimum ring shank 0.083 in. or smooth shank 0.091 in. Length not less than 3/4 in. into roof sheathing.
viii. Fasteners for underlayment are 0.035 in. plastic edge cap with minimum 1 in. diameter—minimum ring shank 0.083 in. or smooth shank 0.091 in. Length is sufficient to penetrate the roof sheathing or not less than 3/4 inches into roof sheathing. Fasteners are corrosion resistant.
f. High-Wind Roof Covering
i. Asphalt shingles are high-wind rated.
ii. Product used to seal drip edge is self-adhering starter strip or flashing cement.
iii. All roof coverings are rated for site-specific wind speed and design pressures.
iv. Base flashing against a vertical sidewall is continuous or step flashing, not less than 4 in. in height and 4 in. in width.
g. Continuous Load Path
i. Structural members and products used to fasten them meet requirements of licensed engineer-designed load path.
ii. Roof sheathing nails are ring/screw shank.
iii. Sheathing for gable end walls is wood structural panels with the same performance category as the walls.
iv. Fastener used to attach roof framing members to wall top plates resists loads in all three directions.
v. Sill plate anchor bolts are 1/2-in diameter. Provide a 3x3-in.-square plate washer at each anchor bolt. 
h. Garage Doors
i. For garage doors without glazed openings (windows), the door assembly (door and all associated hardware and components) meets the design wind pressure for the site OR provide garage door protection with an impact-rated shutter/screen product that meets the design wind pressure for the site.
ii. For garage doors with glazed openings (windows), the door assembly is rated for the design pressure and impact, OR provide garage door protection with an impact-rated shutter/screen product that meets the design wind pressure for the site.
i. Wall System
i. Use reinforced CMU/ICF for exterior walls of the home, running from roof to foundation, including foundation/basement walls, if present.
ii. Vinyl siding complies with the 2017 edition of ASTM D3679 (2017) and has a design wind pressure rating that equals or exceeds the required design wind pressure.
iii. Provide high-wind-rated fiber cement products for exterior cladding and trim. Do not provide vinyl siding.
iv. Fiber cement products and attachment schedules are designed or tested to meet the design wind pressures in the 2018 IRC or ASCE-10.
j. Soffit: Provide fiber cement or wood material for soffits.
k. Roof-Mounted Equipment: Solar PV panels are rated for wind zone and snow/hail as appropriate for location.
7. Criterion 3.10 Resilient Site Design: Flood		Comment by Customization Instructions: Retain if Criterion 3.10 is selected to earn optional points. Retain only the Option selected by the project team. (Note that there are no Product requirements if Option 3 is selected under Criterion 3.10.)	Comment by Customization Instructions: NYC Overlay: All projects located on flood-prone sites as defined by the HPD Design Guidelines are required to comply with Criterion 3.10.
Option 1: ASCE 24-24 Compliance
a. Construction materials (including decks, porches, concrete slabs, garages, storage structures, chimneys, tanks, as applicable) meet standards in ASCE 24-24 and ASCE 7-22 Supplement 2.
b. Barriers (including windows, doors, impermeable panels, flood shields, as applicable) meet dry floodproofing standards in ASCE 24-24 and ASCE 7-22 Supplement 2.
Option 2: HUD One-Pagers for Water	Comment by Customization Instructions: Retain only the specifications below which are applicable based on selected HUD strategies (all strategies under Connectors and Fasteners are required if Option 2 is chosen).
c. Wall Assembly
i. Use flood-resistant materials referenced in FEMA Fact Sheet 1.7 or Table 2 of FEMA Technical Bulletin 2.
ii. Interior gypsum board is non-paper-faced.
iii. Screws used to fasten interior gypsum board are galvanized.
iv. Provide closed-cell foam spray foam insulation for interior wall insulation.
v. For exterior wall cladding, use a drainage plane material designed to be used behind the cladding.
vi. Exterior cladding and trim is vinyl or cement-based.
vii. When using vinyl- and cement-based cladding systems, use a solid sheathing, such as oriented strand board (OSB), behind the drainage plane material. 
d. Connectors and Fasteners
i. For connectors at least 3,000 feet  from coastal areas: use a zinc-galvanized coating, 22-gauge minimum (G90), for connectors. Nails, bolts, washers, and other fasteners should meet ASTM A153 standards for coating thickness. 
ii. For connectors within 3,000 feet of coastal areas: use 16-gauge hot dipped galvanized connectors (G185) meeting ASTM F2329 standards or stainless steel connectors meeting ASTM A240 or A580 standards for connectors.
8. Criterion 3.11 Resilient Site Design: Wildfire		Comment by Customization Instructions: Retain if Criterion 3.11 is selected to earn optional points:
 a. through c. apply for all projects
 d. through h. apply only for projects earning 12 points
a. Roof covering materials are Class A fire-rated.
b. Soffits are noncombustible.
c. Windows are dual-pane, triple-pane, and/or have at least one tempered glass pane.
d. Vegetation planted within 5-30 feet of each building (ignition zone 1) is fire-resistant/high-moisture.
e. Non-vegetated landscaping ground cover used within 5-30 feet of each building (ignition zone 1) is non-flammable.
f. Metal mesh covering vents has 1/8-inch openings.
g. Siding and cladding materials are ignition-resistant (e.g., fiber cement, stucco, brick, steel).
h. Materials used in deck and balcony construction are noncombustible (e.g., tile, metal, concrete).
Water
9. Criteria 4.1 Water-Conserving Fixtures and 4.2 Advanced Water Conservation	Comment by Customization Instructions: NYC Overlay: Criterion 4.2 is required.
a. New installed toilets, showerheads, and lavatory faucets are WaterSense-certified. 	Comment by Customization Instructions: Delete a. and b. if Criterion 4.2, Option 2: Whole-home water certification is selected to earn optional points.
b. All installed products meet water efficiency requirements as established by the project team’s water consumption reduction calculations.
c. All installed products meet water efficiency requirements necessary to achieve whole-home WaterSense certification.	Comment by Customization Instructions: Delete if Criterion 4.2, Option 2: Whole-home water certification is not selected to earn optional points.
10. Criterion 4.3: Water Quality
a. Replacement service pipes, fittings, solders, and/or flux products are lead-free.	Comment by Customization Instructions: Retain if project is:
Substantial Rehab constructed before 1986
Substantial Rehab constructed in 1986 or later, and this requirement is selected for optional points.
Moderate Rehab, and this requirement is selected for optional points.
b. If water testing and remediation is performed: 	Comment by Customization Instructions: Retain if project selects this requirement to earn optional points. 

Retain only the items below which are selected for optional points and applicable based on test results.
c. If lead remediation is required (test results show < 5ppb):
i. Dwelling unit water faucet filters meet NSF/ANSI 58 or NSF/ANSI 53.
d. If lead remediation is required (test results show ≥ 5 ppb):
i. Replacement fixtures certified under WaterSense and/or NSF 61.
11. Criterion 4.4:  Monitoring Water Consumption and Leaks		Comment by Customization Instructions: Retain if Criterion 4.4, Option 3: Advanced Water Metering, is selected to earn optional points.
a. Water meters are remote-readable and provide alerts and data logging at less than 5-minute intervals. Meters are capable of separately metering cold-water branches serving individual dwelling units, cold-water risers and feed for all buildings in the project, common laundry, toilets, boiler makeup water, outdoor water consumption, and/or water consumption in nonresidential spaces as applicable.
12. Criterion 4.5: Efficient Plumbing Layout and Design	Comment by Customization Instructions: Retain if Criterion 4.5 is selected for optional points. If Criterion 4.5 is selected, item a. is always required. 

For remaining items, retain only those which are selected for optional points. 	Comment by Customization Instructions: NYC Overlay: Criterion 4.5 is required.
a. In-unit recirculation pumps (if installed) are demand-initiated by motion or push button, not activated solely based on a timer and/or temperature sensor.
b. Option 1: Performance Design Path: Hot water distribution pipe diameter meets IAPMO Water Demand Calculator via 2023 WE-Stand Chapter 5 or 224 UPC Appendix M.
c. Option 2: Certification Design Path: All installed products meet water efficiency requirements necessary to earn certification under WaterSense Labeled Homes Version 2.0.
d. Option 3: Volumetric Design Path, Strategy A: Hot water distribution pipe diameter sized to store no more than 0.5 gallons of water in any piping/manifold between the fixture and the hot water source (i.e., the water heater or, if present, the central recirculation line/riser pipe).
e. Option 3: Volumetric Design Path, Strategy B
i. Hot water distribution pipe diameter sized to store no more than 1.8 gallons of water in any piping/manifold between the fixture and the hot water source (i.e., the water heater or, if present, the central recirculation line/riser pipe).
ii. Water heater has a UEF ≥ 0.87 for gas or UEF ≥ 2.2 for electric.
iii. Dwelling unit showerheads, bath faucets, and aerators are WaterSense certified.
iv. Pipe insulation for central recirculating hot water distribution system:
a. If pipe is less than 1.5 inches in diameter: at least 1.5 inches thick (or at least R-10)
b. If pipe is at least 1.5 inches in diameter: at least 2 inches thick (or at least R-12)
13. Criterion 4.6: Indoor Water Efficiency - Nonpotable Water Reuse	Comment by Customization Instructions: Retain if Criterion 4.6 is selected to earn optional points.
a. Rain/greywater distribution pipes are purple-colored PVC or PE pipe, clearly labeled as non-potable water, or meet all requirements of local building and health codes.
b. Storage/surge tanks are water-tight and corrosion-resistant with tamper-resistant lid installed at or above grade and a permanent, gravity-fed connection to the building sewer for overflow, protected by a backwater valve. Clearly labeled as non-potable water.
c. Diverter valves clearly marked to indicate potable and non-potable water sources.
d. Filtration and treatment units for rain/greywater system meet all requirements of local building and health codes.
14. Criterion 4.7: Access to Potable Water During Emergencies		Comment by Customization Instructions: Retain if Criterion 4.7, Options 2: On-site water storage or 3: On-site well, are selected to earn optional points. Retain only the option selected by the project team.	Comment by Customization Instructions: NYC Overlay: Delete this Criterion
a. Option 2: If provided, on-site potable water storage tank provides at least 10 gallons per resident for four days. 
b. Option 3: On-site well pumping equipment can be operated when the electric grid is down (e.g., with a hand pump, portable generator, or gravity flow).
Energy
15. Criterion 5.2a: Building Performance	Comment by Customization Instructions: Retain if project is:
New Construction
NOT using Criterion 5.3, Option 2
Select program based on building type.
a. All products meet ENERGY STAR Multifamily New Construction program requirements.
16. Criterion 5.2b: Building Performance	Comment by Customization Instructions: Retain if project is:
Substantial Rehab
Moderate Rehab
NOT using Criterion 5.3, Option 2
Retain only the option selected by the project team.
a. Option 1: Energy Rating Index: All installed products meet energy efficiency requirements necessary for dwelling units to earn an ERI score of [80 / 90] or less, as indicated by the qualified Rater per ANSI/RESNET/ICC 301.	Comment by Customization Instructions: Select ERI target based on project type:
Moderate rehab pre-1980: 90
Substantial rehab or moderate rehab post-1980: 80
b. Option 2: ASHRAE 90.1: All installed products meet energy efficiency requirements necessary for project energy performance to be equivalent or better than ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016. 
c. Option 2: Project in California: All installed products meet energy efficiency requirements necessary for project to achieve energy performance equivalent to or better than the version of Title 24 under which the project is permitted.
d. Projects using Energy Outreach Colorado Program: All installed products meet energy efficiency requirements necessary for project to achieve energy performance equivalent to or better than the requirements of Energy Outreach Colorado.
e. Newly installed HVAC equipment meets sizing calculations in accordance with the Air Conditioning Contractors of America (ACCA) Manuals J and S or ASHRAE handbooks
f. 90% of permanently installed lights are LEDs.
g. Installed clothes washers, dishwashers, and refrigerators are ENERGY STAR certified.
h. NYC Overlay: All products meet requirements of the New York City Prescriptive Pathway for Tenant in Place Rehabs.	Comment by Customization Instructions: NYC Overlay: Eligible projects may comply with this mandatory criterion by following the NYC Prescriptive Pathway for Tenant in Place Rehabs. If this option is selected, delete all other specifications under this Criterion.
17. Criterion 5.3: Advanced Building Performance		Comment by Customization Instructions: Retain if Criterion 5.3 is selected for points. Retain only the option selected by the project team.
If Option 2 is selected, delete Criterion 5.2a/b above.
a. Option 1: Performance Above Mandatory Requirement (New Construction): All installed products meet energy efficiency requirements necessary for each dwelling unit to achieve an ERI score at least 5 points more efficient than ENERGY STAR Multifamily New Construction program's ERI Target Score, as indicated by the qualified Rater per ANSI/RESNET/ICC 301, or at least 5% more efficient than the program's ASHRAE target.
b. Option 1: Performance Above Mandatory Requirement (Rehabilitation, ERI Path): All installed products meet energy efficiency requirements necessary for dwelling units to earn an ERI score of [75 / 85] or less, excluding on-site power generation.	Comment by Customization Instructions: Select ERI target based on project type:
Substantial rehab with no historic designation: 75
Moderate rehab or substantial rehab with historic designation: 85
c. Option 1: Performance Above Mandatory Requirement (Rehabilitation, ASHRAE Path): All installed products meet energy efficiency requirements necessary for project energy performance to be at least 5% better than ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016, excluding on-site power generation.
d. Option 1: Performance Above Mandatory Requirement (Rehabilitation, Title 24 Path): All installed products meet energy efficiency requirements necessary for project energy performance to be at least 5% better than the version of Title 24 under which the project is permitted.
e. Option 2: Advanced Building Certification (DOE Efficient New Homes): All products meet DOE Efficient New Homes program requirements for the program version applicable based on project type and permit date.
f. Option 2: Advanced Building Certification (ENERGY STAR NextGen): All products meet ENERGY STAR NextGen program requirements.
g. Option 2: Advanced Building Certification (Passive House International): All products meet Passive House International Classic, Plus, Premium, LEB, or EnerPHit program requirements.
h. Option 2: Advanced Building Certification (Phius): All products meet Phius CORE, ZERO, or REVIVE program requirements.
i. Option 3: Deep Energy Retrofit (Rehabilitation, ERI Path): All installed products meet energy efficiency requirements necessary for dwelling units to earn an ERI score of [65 / 75] or less, excluding on-site power generation.	Comment by Customization Instructions: Select ERI target based on project type:
Substantial rehabs: 65
Moderate rehab: 75
j. Option 3: Deep Energy Retrofit (Rehabilitation, ASHRAE Path): All installed products meet energy efficiency requirements necessary for project energy performance to be at least [10% / 15%] better than ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016, excluding on-site power generation.	Comment by Customization Instructions: Select target based on project type:
Substantial rehabs: 15%
Moderate rehabs: 10%
k. Option 3: Deep Energy Retrofit (Rehabilitation, Title 24 Path): All installed products meet energy efficiency requirements necessary for project energy performance to be at least [10% / 15%] better than the version of Title 24 under which the project is permitted.	Comment by Customization Instructions: Select target based on project type:
Substantial rehabs: 15%
Moderate rehabs: 10%
18. Criterion 5.4: All-Electric and Electric-Ready Design		Comment by Customization Instructions: Retain if project is:
New Construction
Rehab, and Criterion 5.4b is selected to earn optional points
Retain only the Option selected by the project team.	Comment by Customization Instructions: NYC Overlay: New construction projects are required to be all-electric. Rehabs have a third option to earn optional points under this Criterion: electric space heating and cooling.
Option 1: Electric Ready
a. Cooking equipment is electric.
b. Branch circuit for future electric space heating uses 3-conductor, 10AWG copper wire.	Comment by Customization Instructions: Retain if project contains non-electric, in-dwelling space heating.
c. Branch circuit for future electric water heating uses 3-conductor, 10AWG copper wire.	Comment by Customization Instructions: Retain if the project contains non-electric, in-dwelling water heating.
Option 2: All-Electric
d. Cooking, space heating, and water heating equipment are electric.
NYC Overlay Option 3:
e. Space heating and cooling equipment are electric.
19. Criterion 5.5: Peak Demand Control		Comment by Customization Instructions: Retain if Criterion 5.5 is selected to earn optional points. Retain only the option selected by the project team.
a. Option 1: Hot-Water Thermal Storage and Control: Hot water system has sufficient capacity, storage, and controls to meet hot-water demand from storage alone during region's peak hours.
b. Option 2: Residential Demand Management: Energy management and monitoring products (including smart thermostats, energy monitors, smart electric panels, etc.) meet requirements of residential demand management plan for in-unit residential electrical loads.
20. Criterion 5.6: Backup Power		Comment by Customization Instructions: Retain if Criterion 5.6, Options 1 or 2 are selected to earn optional points. Retain only the option selected by the project team. The first specification (a.) is required for both options.
a. Battery storage has programming capable of switching on when electric grid goes down.
b. Option 1: Islandable PV + Battery Storage: Solar photovoltaic system is islandable (can continue operating and providing energy when the grid goes down).
c. Option 2: Off-peak Battery Storage: Battery energy storage system is capable of storing off-peak energy.
21. Criterion 5.7: Renewable Energy	Comment by Customization Instructions: Retain if Criterion 5.7, Option 1, Strategy C is selected to earn optional points.
a. On-site geothermal energy system is designed to provide at least 30% of total building site energy use.
22. Criterion 5.8: Electric Vehicle Charging	Comment by Customization Instructions: Retain if project is :
New Construction
Substantial Rehab
Moderate rehab, and selecting Criterion 5.8 to earn optional points. 
Delete if project does not use an ALMS.
a. Installed EVSE connected to an Automatic Load Management System (ALMS) has a minimum capacity of 30 amperes.
23. Criterion 5.9: Passive Survivability		Comment by Customization Instructions: Retain if Criterion 5.9, Option 1: Passive Cooling, is selected to earn optional points. Retain only the strategy selected by the project team.
a. Natural Ventilation Strategy: Dwelling unit windows are operable and equipped with an insect screen (at least one window per dwelling unit).
b. Shading Strategy: Interior blinds in south-facing windows are insulated and have a full-perimeter track.
Materials
24. Criterion 6.1: Product Category Screening		Comment by Customization Instructions: Retain if Criterion 6.1 is selected to earn optional points.
a. Products selected based on results of Product Category Screening Template for embodied carbon and material health.
25. Criterion 6.2: Reduction of Materials and Waste		Comment by Customization Instructions: Retain only the strategies selected to comply with mandatory requirements or to earn optional points.
a. Strategy D: 50% of building square footage integrates off-site, prefabricated volumetric, or panelized manufacturing.
b. Strategy E: 15% of the entire product category below is salvaged:
i. [insert product category / Contractor may select product type.]
c. Strategy J: Specify products with extended producer responsibility programs (e.g., take-back programs).
d. Strategy L: Use modular construction that is also designed for disassembly.
26. Criterion 6.4: Advanced Material Selection		Comment by Customization Instructions: Retain all mandatory requirements and strategies selected to earn optional points.
a. All adhesives and sealants applied inside the air barrier meet VOC limits provided by the most recent version of SCAQMD 1168.
As of October 9, 2025, maximum VOC limits are:
i. Carpet pad adhesives: 50 g/L
ii. Wood flooring adhesives: 120 g/L
iii. Rubber floor adhesives: 60 g/L
iv. Subfloor adhesives: 50 g/L
v. Vinyl composition tile and asphalt tile adhesives: 50 g/L
vi. Drywall and panel adhesives: 50 g/L
vii. Cove base adhesives: 50 g/L
viii. Multipurpose construction adhesives: 70 g/L
ix. Structural glazing adhesives: 100 g/L
x. Structural wood member adhesives: 140 g/L
xi. Architectural sealants - clear, paintable, and immediately water-resistant: 250 g/L
xii. Architectural sealant primers - nonporous: 250 g/L
xiii. Architectural sealant primers - porous: 775 g/L"
b. 80% (by volume) of adhesives and sealants applied inside the air barrier meet the CDHP Standard Method for the school or residential scenario.
c. Cladding: Exterior wall cladding is made up of one or a combination of the following: preserved or repaired existing cladding; expanded cord board; natural wood (including heat treated), bamboo, engineered wood, thin brick, natural stone, ceramic, terra-cotta, lime plaster, or fiber cement.
d. Concrete: 90% of newly installed concrete has a GWP [no higher than / 20% lower than] the regional average. 	Comment by Customization Instructions: Select target based on points claimed:
2 points: No higher than regional average
5 points: 20% lower than the regional average.
i. Regional average GWP may be determined using the most recent Carbon Leadership Forum North American Material Baselines report or using regional industry-average environmental product declarations (EPDs) to determine typical impact values per concrete strength class in the property’s location.
e. Flooring	Comment by Customization Instructions: Option 1 or 2 must be selected under Flooring.
i. Option 1: Best-in-class: 90% of all flooring is made up of one or a combination of the following: repaired existing floor; linoleum; solid wood flooring that is FSC-certified or salvaged wood; pre-finished engineered wood or bamboo; pre-finished cork (excluding rubber/cork composite); no floorcovering (e.g., concrete or CLT structural slab without a finish or sealer); ceramic/porcelain tile (no added lead)
ii. Option 2: Minimum Standard: All flooring products are either an inherently non-emitting source of VOCs (such as unfinished stone or porcelain tile) or have VOC emissions verified as meeting the requirements of the CDPH Standard Method for school or residential scenarios.
For additional points: 	Comment by Customization Instructions: Teams may select either, both, or none of these strategies.
a. All flooring adhesives, coating, and sealants, whether pre-applied or site-applied, do not contain PFAS. 
b. Site-applied flooring adhesives, coatings, and sealants meet CDPH Standard Method emission requirements and do not contain epoxy or polyurethane.
f. Gypsum Wallboard: At least 60% of all newly installed interior gypsum wallboard is lightweight gypsum board and meets CDPH Standard Method emission requirements.
g. Insulation	Comment by Customization Instructions: Option 1, 2, or 3 must be selected under Insulation. All project must comply with the first specification in this section (i.).
i. Mineral wool batt insulation (if used) is formaldehyde free.
Option 1: Best-in-class
ii. Foam insulation (if used) has blowing agents with low global warming potential (GWP150)
iii. At least 75% of all newly installed above-grade insulation (exterior and interior) is bio-based, such as wood fiber, hemp fiber, cellulose or cotton, hempcrete, or straw.
Option 2: Intermediate
iv. At least 90% of all newly installed above-grade insulation (exterior and interior) is bio-based (wood fiber, hemp fiber, cellulose or cotton, hempcrete, or straw), fiberglass batts, mineral wool batts, and/or unfaced fiberglass or mineral wool boards.
Option 3: Minimum
i. Foam insulation (if used) has blowing agents with low global warming potential (GWP150)
h. Paint and other coatings, wet-applied interior	Comment by Customization Instructions: Option 1, 2, or 3 must be selected under Paint and Other Coatings.
Option 1: Best-in-class
i. At least 50% (by cost or volume) of all paints are mineral paint, such as lime or mineral silicate.
a. 90% (by cost or volume) of the remaining paints, coatings, and primers have VOC content less than or equal to thresholds in the most recent version of SCAQMD 1113 and VOC emissions are compliant with the CDPH Standard Method for school or residential exposure scenarios.
Option 2: Intermediate
ii. At least 90% (by cost or volume) of interior paints, coatings, and primers are free of PFAS and alkylphenol ethoxylates (APEs), or are mineral paints.
a. These paints, coatings, and primers must also meet VOC content thresholds in the most recent version of SCAQMD 1113 and have VOC emissions compliant with the CDPH Standard Method for school or residential exposure scenarios.
Option 3: Minimum
iii. VOC content of all interior paints, coatings and primers is less than or equal to the thresholds in the most recent version of SCAQMD 1113.
iv. 90% (by volume) of all interior pants, coatings, and primers are verified as compliant with CDPH Standard Method for school or residential exposure scenarios.

As of October 9, 2025, maximum VOC limits in SCAQMD 1113 are:
i. Primers, sealers, and undercoatings: 100 g/L
ii. Coatings, flats and non-flats, and floor: 50 g/L
iii. Rust-preventative coatings: 100 g/L
iv. Wood coatings: 275 g/L
v. Stains, interior: 250 g/L
vi. Tub and tile refinishing coatings: 420 g/L

i. Steel
i. Option 1: Best-in-class: 100% of steel produced by electric-arc furnace (instead of by blast furnace or basic oxygen furnace) and/or with at least 90% recycled content.
ii. Option 2: Intermediate: 75% of steel deck, cold-formed steel framing, and structural steel has a GWP at least 20% lower than baseline as indicated in the most recent Carbon Leadership Forum North American Material Baselines report.
j. All hardwood plywood, particleboard, medium-density fiberboard (MDF), and these materials within other products (e.g., cabinets and doors) have formaldehyde emissions less than or equal to the thresholds provided by California Air Resources Board (CARB) Phase II Composite Wood Products Airborne Toxic Control Measure and/or Toxic Substances Control Act (TSCA) Title IV.
For additional points:	Comment by Customization Instructions: Teams may select either, both, or none of these strategies.
i. All hardwood plywood, particleboard, medium-density fiberboard (MDF), and these materials within other products (e.g., cabinets and doors) have no added formaldehyde (NAF).	Comment by Customization Instructions: If this strategy is selected to earn optional points, item j., above, is not required.
ii. At least 50% of hardwood plywood, particleboard, medium-density fiberboard (MDF), and these materials within other products (e.g., cabinets and doors) are certified to the Forest Stewardship Council (FSC) standard.
k. Wood, noncomposite: At least 50% of noncomposite wood installed as part of the project is certified to the Forest Stewardship Council standard.
Healthy Living Environment
27. Criterion 7.2: Clean Air - Combustion Equipment		Comment by Customization Instructions: Retain if project includes any combustion equipment, unless combustion equipment is located only in detached utility buildings or non-enclosed spaces.  
a. Carbon monoxide alarms are hard-wired with battery backup.
b. New combustion appliances, water heating, and space heating equipment is power-vented or direct-vented.
28. Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	Comment by Customization Instructions: Delete if project:
Does not have a parking garage
Has a mechanically vented garage
Only has open parking structures
a. Carbon monoxide alarms are hard-wired with battery backup.
29. Criterion 7.5: Clean Air - Ventilation	Comment by Customization Instructions: Retain if project is:
New construction 
Substantial rehab
Moderate rehab, and Criterion 7.5 is selected to earn optional points. For Moderate rehabs, retain only the options selected to earn points by the project team.
a. In-unit kitchen mechanical exhaust system(s) comply with ASHRAE 62.2-2022, sections 5 and 7.
i. Or, if no combustion-fueled appliances are located within the dwelling unit, heat- or energy-recovery ventilator or a ceiling- or wall-mounted fan exhausts kitchen air to the outdoors with a continuous rate of 5 ACH or 25 CFM (per Table M1507.3 of the 2009 International Residential Code).	Comment by Customization Instructions: Retain if Criterion 5.3, Option 2: Advanced building certification is selected to earn optional points.
b. Bathroom mechanical exhaust system(s) comply with ASHRAE 62.2-2022, sections 5 and 7. Fans serving individual bathrooms are ENERGY STAR certified.
i. If bath fans do not run continuously, provide controls that ensure adequate run time.
c. Whole-house mechanical ventilation system complies with ASHRAE 62.2-2022, sections 4 and 7 (excluding section 4.2).
d. Mechanical ventilation system(s) serving hallways, stairwells, and common/amenity spaces comply with ASHRAE 62.2-2022.	Comment by Customization Instructions: Retain if project is four stories or more.
e. For systems delivering 2,000 CFM or more of outdoor air, provide data logging equipment and alarms capable of providing real-time air-volume measurements to indicate when flow varies by +/- 15% of design value.
30. Criterion 7.6: Clean Air - Indoor Air Filtration		Comment by Customization Instructions: Retain if new central HVAC system is installed.
a. Filter for newly-installed central forced-air HVAC system is at least MERV 13.
31. Criterion 7.7: Clean Air - Enhanced IAQ	Comment by Customization Instructions: Retain if Criterion 7.7, Option 2: Indoor AirPlus is selected to earn optional points.	Comment by Customization Instructions: NYC Overlay: This Criterion is required, and may be met using Option 1 or Option 2 (Indoor AirPlus).
a. All products meet the requirements of the EPA Indoor AirPlus program.
32. Criterion 7.8: Moisture - Dehumidification		Comment by Customization Instructions: Retain if project is:
Located in CZ 1A, 2A, 3A, or 4A, and has selected Criterion 5.3 to earn optional points. 
Located in any CZ, and selected Criterion 7.8 to earn optional points.
Retain only the Option selected by the project team.
a. Option 1: Dedicated Dehumidification System: Supplemental dehumidification equipment is capable of keeping relative humidity at or below 60%.
b. Option 3: ERV or HRV	Comment by Customization Instructions: NYC Overlay: Option 3 is required for projects following Criterion 5.3.
i. Energy-recovery ventilator (ERV) includes moisture recovery.
ii. Unitized ERV system must have the capability to boost flow rates during periods of high interior humidity.
iii. Centralized ERV system must have the capacity to partially bypass the energy-recovery core or slow down the enthalpy wheel during periods of high interior humidity.
33. Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction		Comment by Customization Instructions: Retain if project is new construction.
a. Polyethylene sheeting used as a vapor retarder beneath any new or replacement concrete slabs (including basements, crawl spaces, or slab on grade construction) shall be at least 6mm thick.
b. Polyethylene sheeting used as a vapor retarder in crawl spaces (with no concrete slab) shall be at least 8mm thick and cross-laminated.
34. Criterion 7.10 Managing Moisture: Bath, Kitchen, and Laundry Assemblies	Comment by Customization Instructions: Retain if project is:
New construction
Substantial rehab
Moderate rehab, and bathroom kitchen, and/or laundry is in scope. For Moderate rehabs, only retain items in this section which are applicable based on scope of work.
a. Cement board or fiber-cement board installed behind tub and shower enclosures (excluding one-piece fiberglass tubs or shower enclosures) meet one of the following:
i. ASTM C1288
ii. ISO 8336, Category C
iii. Listed as an acceptable material in the ENERGY STAR MFNC National Water Management System Requirements
b. Cement board or fiber-cement board installed behind tub and shower enclosures is not paper-faced.
c. Materials used for surfaces throughout bathrooms, kitchens, and laundry rooms are durable, cleanable, and are not prone to deterioration due to moisture intrusion.
35. Criterion 7.11: Reducing Allergens and Disease Vectors - Integrated Pest Management	
a. Caulking used to seal wall, floor, and joint penetrations is low VOC.
b. Screens used to cover openings greater than 1/4 inch are rodent- and corrosion-proof, made of copper, stainless steel mesh, or rigid metal cloth.
36. Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	Comment by Customization Instructions: Retain if project is New Construction and Criterion 7.12a is selected to earn optional points. Retain only the Option(s) selected by the project team.
Option 1: Outdoor Noise Abatement
a. Exterior walls have composite Outdoor-Indoor Transmission Class (OITC) rating of at least 40.
b. Windows have Outdoor-Indoor Transmission Class (OITC) rating of at least 30.
Option 2: Indoor Sources of Noise
c. Separation walls have Sound Transmission Class (STC) rating of at least 50 or Apparent Sound Transmission Class (ASTC) of at least 45.
d. Floor and ceiling assemblies between dwelling units have Impact Insulation Class (IIC) rating of at least 50 or Apparent Impact Insulation Class (AIIC) of at least 45.
37. Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation		Comment by Customization Instructions: Retain if project is substantial or moderate rehab and Criterion 7.12b is selected to earn optional points. Retain only the Option(s) selected by the project team.
Option 2: Outdoor Noise Abatement - Minimal Approach
a. Exterior walls have composite Outdoor-Indoor Transmission Class (OITC) rating of at least 40.
b. Windows have Outdoor-Indoor Transmission Class (OITC) rating of at least 30.
Option 2: Outdoor Noise Abatement - Advanced Approach
c. Exterior walls have composite Outdoor-Indoor Transmission Class (OITC) rating of at least 45.
d. Windows have Outdoor-Indoor Transmission Class (OITC) rating of at least 35.
Option 3: Interior Sources of Noise in Bedrooms
e. Grade A: Bedroom party walls meet requirements of ICC G2-2010 Guideline for Acoustics, Grade A.
f. Grade B: Bedroom party walls meet requirements of ICC G2-2010 Guideline for Acoustics, Grade B.
38. Criterion 7.13: Personal and Social Safety		Comment by Customization Instructions: Retain if project is:
New Construction 
Substantial rehab
Retain only the strategies selected by the project team.
a. Strategy D: Barriers, fences, and gates surrounding the property balance security with connection to the surrounding community, avoiding tall, fortress-like fences or walls.
b. Strategy I (more than 12 units): Package storage or lockers can be locked.
c. Strategy I (fewer than 12 units): Mailboxes can be locked.
39. Criterion 7.14: Social Connection and Accessibility - Design for All Ages/Abilities		Comment by Customization Instructions: Retain only the strategies selected by the project team to fulfill this mandatory requirement.
a. Strategy A: Signage for wayfinding throughout the interior and exterior of the property is clear, multilingual (where appropriate) and incorporates illustrations and color.
b. Strategy A: Floor finishes in common spaces and at least 25% of dwelling units have subtle, neutral patterns and plain matte finishes.
c. Strategy C: Light switches in common spaces and 25% of dwelling units contrast in color and value with wall surfaces and have an indicator light when turned off.
d. Strategy D: Furniture used in common spaces is easily movable and not permanently fixed to any surface.
e. Strategy H: Hard-surface floor finishes in common spaces, hallways, entryways, and outdoor pathways are slip-resistant.
f. Strategy I: Bathroom towel bars in 25% of dwelling units support the same loads that grab bars are required to support by code.
g. Strategy J: Faucets in all common spaces and 25% of all faucets in dwelling units are anti-scald or thermostatic (e.g., kitchen, bath, utility sink, as applicable).
h. Strategy L: 
i. Lever door handles for interior and exterior doors in at least 25% of dwelling units.
ii. Drawer and cabinet hardware requires no grasping, pinching, or twisting of the wrist, or small knobs, for 25% of dwelling units.
iii. Faucets in all common spaces and 25% of dwelling units are single-lever.
iv. Light switches in common spaces and 25% of dwelling units are rocker or large-paddle.
40. Criterion 7.15: Access to Nature and Biophilic Design		Comment by Customization Instructions: Retain if Criterion 7.15 is selected to earn optional points. Retain only specs selected by project team for points.
a. Interior materials in dwelling units meet biophilic design requirements (natural materials/patterns that mimic nature).
b. Lighting systems in dwelling units shift with natural daylight cycles and can be controlled by residents.
c. Vegetation in usable outdoor spaces is native and/or culturally significant vegetation and varies seasonally.
41. Criterion 7.16: Healing-Centered and Culturally Responsive Design		Comment by Customization Instructions: Retain if Criterion 7.16 is selected to earn optional points. Retain only specs selected by project team for points.
a. Community-Generated Art: Artwork installed in shared indoor or outdoor spaces is created by or in collaboration with residents and/or local artists and reflect the community that will be served or has historically lived in the community.
b. Storytelling Through Space: Installed products and/or space labels meet requirements of design and names selected by community members.
42. Criterion 7.17 Active Design: Promoting Physical Activity		Comment by Customization Instructions: Retain if Criterion 7.17, Option 1: Encouraging everyday stair use, is selected to earn optional points. Retain only specs selected by project team.

Buildings that include stairs as the only means to travel from one floor to another are not eligible for this option.
a. Finishes in stairways are consistent with, or better than, those in the building corridors.
b. Transparent Glazing: Glazing in doors or adjacent sidelite is transparent and at least 10 square feet in size.
[bookmark: _Toc233209876]Part 3 - Execution
3.1  Enterprise Green Communities - General
1. Meet all Mandatory criterion and all Optional criterion as identified and specified by the design team, as required to achieve certification through Enterprise Green Communities, including following the education plans developed by the project team for the contractor, subcontractors, and consultants to ensure that those working on the jobsite fully understand their role in achieving the project objectives for Green Communities certification. Coordination between installation contractors and testing and verification contractors as needed to ensure compliance with requirements.
3.2 Execution Requirements
1. Location and Neighborhood Fabric
50. Criterion 2.1: Ecological Conservation and Safer Sites	Comment by Customization Instructions: Retain if site includes endangered/threatened plant or animal habitat.
1. Per site plan and construction documents, do not extend built area into habitats for threatened or endangered plant or animal species.
1. Minimize disturbance to habitats for threatened or endangered plant or animal species during construction.
50. Criterion 2.2: Connections to Existing Development and Infrastructure		Comment by Customization Instructions: Retain if project is New Construction and in an Urban/Suburban location.
2. Install all features indicated in site plan and construction documents to connect to adjacent existing developments and roadways, pedestrian networks, and bikes paths and lanes.
50. Criterion 2.5: Access to Open Space		Comment by Customization Instructions: Retain if Criterion 2.5, Option 2: On-site open space, is selected to earn optional points.
3. Follow paving guidance according to site plan - including at least 80% non-paved surfaces for space designated as "on-site open space."
50. Criterion 2.6: Transit, Mobility, and Walkability	Comment by Customization Instructions: Retain if Criterion 2.6 is selected to earn optional points. Retain only the strategies selected by the project team.
4. Install vehicle-share and/or vanpool parking on the property, indicated with pavement markings or signage.
4. Install outdoor short-term bicycle storage or racks and one bike-repair station accessible for visitors and residents.
4. Install secure, lockable, sheltered, and accessible long-term bicycle storage for at least 25% of building residents. Post signage directing residents to bicycle parking areas.
4. Install public wayfinding signage that promotes walkability and access to services.
4. Install at least two site-improvement features adjacent to sidewalk(s) within the development (e.g., street trees, seating, trash receptacles, or bike-maintenance stations):
5. [insert features / Contractor may select features.]
4. Install at least two of these features within the development, as indicated by the construction documents and project team:	Comment by Customization Instructions: Retain only the features selected by the project team.
6. Curb extensions
6. Sidewalk(s) widened beyond what is required by code or local regulation
6. An unpaved buffer separation, barrier, or curb edge to physically separate sidewalks from roadways
6. Visual appearance of sidewalks where they cross driveways and alley access-ways, using a scoring pattern or special paving
6. Clearly defined and marked crosswalks at all intersections
50. Criterion 2.9: Access to Broadband	
5. Install broadband internet service with at least a speed of 100 megabits per section for downloading and 20 megabits per second for uploading to each common space and residential unit.	Comment by Customization Instructions: Retain if Criterion 2.9 is selected to earn optional points. If this option is selected, delete remaining specifications under this Criterion.
5. Install broadband internet service with at least a speed of 100 megabits per section for downloading and 20 megabits per second for uploading to one shared common space (if present).	Comment by Customization Instructions: Retain for multifamily projects where 100/20 fixed broadband is available to the parcel.
5. Install broadband conduit from property line at the expected broadband access point to the utility room. 	Comment by Customization Instructions: Retain c. and d. for multifamily projects where 100/20 fixed broadband is not available to the parcel.
5. Install broadband conduit from the utility room through risers and/or other infrastructure that leads to the expected network termination points, to at least: 
4. One common space (if present)
4. Expected network termination point in each dwelling unit and each common space (if present)
50. Criterion 2.10: Adaptive Reuse of Buildings		Comment by Customization Instructions: Retain if Criterion 2.10 is selected to earn optional points.
6. Adapt, renovate, or reuse at least 50% of the existing structure and envelope, including exterior skin and framing but excluding window assemblies and nonstructural roofing.
1. Site Design
51. Criterion 3.1: Minimization of Disturbance During Staging and Construction
1. Execute erosion and sedimentation control plan, including the following strategies: 	Comment by Customization Instructions: Retain if project is 1 acre or smaller.
1. Stockpile and protect high-quality site soils to be reused.
1. Control the path and velocity of runoff with silt fencing or comparable measures.
1. Protect ecologically sensitive areas, such as on-site storm sewer inlets, watercourses, and water bodies, by applying straw bales, silt fencing, silt sacks, rock filters, or comparable measures.
1. Provide swales to divert surface water from hillsides.
1. Identify and protect healthy trees with a diameter at breast height greater than 5 inches during construction. Install tree-protection fencing outside the critical root zone. Do not preserve invasive species or trees that present a hazard.
1. If soil in a sloped area is disturbed during construction, use tiers, erosion blankets (geotextile mats), compost blankets, filter socks and berms, or an equivalent approach to keep soil stabilized. The maximum gradient should be consistent with existing natural conditions in the surrounding area. In hot, arid climates, use lesser gradients on south- and west-facing slopes to improve landscape reestablishment and ongoing viability.
1. Execute Environmental Protection Agency (EPA) National Pollutant Discharge Elimination System (NPDES) Construction General Permit for Stormwater Discharges, or local requirements - whichever is more stringent.	Comment by Customization Instructions: Retain if project is larger than 1 acre.
1. Photograph all erosion and sedimentation control measures used throughout construction, including representative photos during rain events (as applicable) to document no visible off-site discharge.
51. Criterion 3.2: Site Design for Ecosystem Services	
2. Any disturbed area that remains undeveloped must be reseeded, planted, or restored to natural conditions. Reseeding and planting must meet product requirements.  
51. Criterion 3.3: Exterior Lighting	Comment by Customization Instructions: Delete Criterion 3.3 if scope does not include exterior lighting. Retain only the lighting zone applicable to the project or the option selected by the project team to earn optional points.
All permanently installed exterior lighting fixtures, with the exception of emergency lighting, must meet the following requirements or local requirements—whichever is more stringent.
		For projects in Lighting Zone 0:
a. All B1 - rated fixtures:
i. Minimum distance to property line: 1 mounting height
ii. If installed less than 2 mounting heights from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All B0 - rated fixtures: 
i. If installed 1 or fewer mounting heights to property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
For projects in Lighting Zone 1:
b. All B3 - rated fixtures:
i. Minimum distance to property line: 2 mounting heights
All B2 - rated fixtures:
i. Minimum distance to property line: 1 mounting height
ii. If installed less than 2 mounting heights from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line.
All B1 - rated fixtures:
i. Minimum distance to property line: 0.5 mounting height
ii. If installed less than 1 mounting height from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All B0 - rated fixtures: 
i. If installed 0.5 or fewer mounting heights to property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All G1 - rated fixtures:
i. Minimum distance to property line: 2 mounting heights, unless mounted with backlight perpendicular to property line.
For projects in Lighting Zone 2:
c. All B4 - rated fixtures:
i. Minimum distance to property line: 2 mounting heights
All B3 - rated fixtures:
i. Minimum distance to property line: 1 mounting height
ii. If installed less than 2 mounting heights from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All B2 or B1 - rated fixtures:
i. Minimum distance to property line: 0.5 mounting height
ii. If installed less than 1 mounting height from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All B0 - rated fixtures: 
i. If installed 0.5 or fewer mounting heights to property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All G2 - rated fixtures:
i. Minimum distance to property line: 2 mounting heights, unless mounted with backlight perpendicular to property line.
All G1 - rated fixtures:
i. Minimum distance to property line: 1 mounting height, unless mounted with backlight perpendicular to property line.
For projects in Lighting Zone 3:
d. All B5 - rated fixtures:
i. Minimum distance to property line: 2 mounting heights
All B4 - rated fixtures:
i. Minimum distance to property line: 1 mounting height
ii. If installed less than 2 mounting heights from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All B2 or B3 - rated fixtures:
i. Minimum distance to property line: 0.5 mounting height
ii. If installed less than 1 mounting height from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All B1 - rated fixtures: 
i. If installed 0.5 or fewer mounting heights to property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line.
All G3 - rated fixtures:
i. Minimum distance to property line: 2 mounting heights, unless mounted with backlight perpendicular to property line.
All G1 - rated fixtures:
i. Minimum distance to property line: 0.5 mounting heights, unless mounted with backlight perpendicular to property line."
For projects in Lighting Zone 4:
e. All B5 - rated fixtures:
i. Minimum distance to property line: 2 mounting heights
All B4 - rated fixtures:
i. Minimum distance to property line: 1 mounting height
ii. If installed less than 2 mounting heights from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All B3 - rated fixtures:
i. Minimum distance to property line: 0.5 mounting height
ii. If installed less than 1 mounting height from the property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All B2 - rated fixtures: 
i. If installed 0.5 or fewer mounting heights to property line, must be mounted with backlight portion of light output oriented perpendicular and towards the property line. 
All G3 or G4 - rated fixtures:
i. Minimum distance to property line: 2 mounting heights, unless mounted with backlight perpendicular to property line.
All G2 - rated fixtures:
i. Minimum distance to property line: 1 mounting heights, unless mounted with backlight perpendicular to property line.
f. Install all exterior lighting according to the DarkSky Luminaires Program, Version 3.0.	Comment by Customization Instructions: Retain if 3.3, DarkSky selected for points. If DarkSky is selected, delete all other items under Criterion 3.3.
g. Install all exterior lighting according to the Florida Fish and Wildlife Conservation Commission (FWC) Guidelines.	Comment by Customization Instructions: Retain if 3.3, FWC selected for points. If FWC is selected, delete all other items under Criterion 3.3.
4. Criterion 3.4 Surface Stormwater Management		Comment by Customization Instructions: Retain if project is:
New construction
Substantial or Moderate Rehab, and land disturbed is greater than 5,000 ft2.
Claiming optional points under Criterion 3.4.
a. Install surface stormwater management features in accordance with the surface stormwater management design.
5. Criterion 3.5 Outdoor Water Use: Efficient Irrigation		Comment by Customization Instructions: Delete if project does not include irrigation or landscaping.
a. After installation of irrigation system, provide contractor with as-built information including zone map, control sequence, shut-off locations, commissioning or test data indicating system is operating as intended, and relevant operations or maintenance task schedules.
b. Coordinate with Electrical to provide power directly to irrigation controllers.  
6. Criterion 3.6 Outdoor Water Use: Alternative Sources	Comment by Customization Instructions: Retain if Criterion 3.6 is selected to earn optional points. Retain only the Option selected by the project team.
a. Option 1: Install irrigation system that integrates rainwater harvesting, reclaimed water, or greywater that offsets 25% or more of total design irrigation water demand.
b. Option 2:
i. Install irrigation system with no sources from potable water.
ii. Install irrigation system sourced only from rainwater.
7. Criterion 3.7: Traffic Safety and Mobility		Comment by Customization Instructions: Retain if project is:
New construction 
Substantial rehab
Moderate rehab using Criterion 3.7 for optional points. 

Retain only the applicable strategies selected by the project team.
a. Pick-up/Drop-off: 
i. Install a smooth, universally accessible sidewalk or path from the residents' pick-up/drop-off area to the building entry and to the public street, including curb ramps and ADA-compliant turning radii at landing.
ii. Install exterior signage indicating the designated pick-up/drop-off area. 
iii. Install seating and lighting in the interior or exterior waiting area designated on the plans. If exterior, waiting area must be covered.
b. Curbless Street: Install contrasting textures, paving patterns, tactile strips, planters, fenceposts, and/or bollards to differentiate and delineate pedestrian-only space from curbless streets.
c. Crossed Paths: 
i. Signage installed where walking/rolling paths or sidewalks cross vehicular driveways, service access, or loading zones, indicating that vehicles should yield to people walking or rolling.
ii. Where bike lanes cross pedestrian paths, mark pavement and/or install signage indicating cyclists must yield to pedestrians.
iii. Mark pavement at the edge of any intersection between a driveway and a sidewalk or bike path. Mark pavement at the edge of any intersection between a bike lane and a pedestrian path. 
d. Roadway: 
i. Install auditory crossing signals for all roadways adjacent to site under the developer's control.
ii. Create access ramps at road crossing with curbs.
e. Roadway-adjacent Sidewalk: For all vehicular roadways adjacent to pedestrian sidewalks, install buffer zone (including street trees and/or landscaping) between sidewalk and roadway. Roadways that include on-street parking adjacent to pedestrian sidewalk are exempt.
f. Hazard-Adjacent Play Space: 
i. Enclose playground or outdoor recreation space with child-safe gate or fence.
ii. Install accessible sidewalk or path from building to recreation space.
8. Criterion 3.8: Heat-Island Management		Comment by Customization Instructions: Retain if project is:
New construction 
Substantial rehab
Moderate rehab using Criterion 3.8 for optional points.
Retain only the Option(s) selected by the project team to meet mandatory requirements or earn optional points.
a. Option 1: Install roofing materials meeting SRI requirements, vegetated roof, and/or PV panels to cover at least 70% of usable roof area.
b. Option 2: Install shade structures, paving materials meeting solar reflectance requirements, and/or open-grid paving systems on at least 50% of ground-level paved areas.
9. Criterion 3.9: Resilient Site Design - Wind		Comment by Customization Instructions: Retain if Criterion 3.9 is selected to earn optional points. Retain only the Option selected by the project team.
Option 1: FORTIFIED Designation
a. Install roof in accordance with FORTIFIED Multifamily requirements, including continuous roof covers, roof deck fasteners, flashing, drip-edge, coping, counter-flashing, wood nailers, gutters, roof deck materials, roof deck attachments, underlayments, ridge vents, skylights, roof-mounted equipment and lighting protection systems, and safety rails.
b. Install wall systems, gable ends, windows, curtain walls, and doors in accordance with the FORTIFIED Multifamily requirements as applicable in hurricane-prone and high-wind-prone regions. 	Comment by Customization Instructions: Retain if FORTIFIED Multifamily Silver or Gold is selected.
c. Continuous load path from roof to foundation of building installed per design of the structural engineer of record.	Comment by Customization Instructions: Retain c. through e. if FORITIFIED Multifamily Gold is selected.
d. Structural members of cantilever overhangs anchored.
e. Canopies, car ports, or any other vehicle-type drive-through structures installed with load path members and connections.
f. Hail guards installed over air conditioner condenser fins, air intakes such as fans, and any other vulnerable component.	Comment by Customization Instructions: Retain if FORTIFIED Multifamily Hail Supplement is selected.
Option 2: HUD One-Pagers for Wind	Comment by Customization Instructions: Retain only the specifications below which are applicable based on selected HUD strategies. At least two items from any single category must be selected in order to earn points for that category.
g. Openings/Shutters
i. Install window shutters.
ii. Install exterior entry doors to swing outward.
iii. Install protection for all glazed openings (windows, patio doors, skylights, glass block, etc.) that are not able to resist wind-borne debris.
iv. Install protection for all exterior door assemblies that are not pressure or impact rated.
h. Roof Deck and Underlayment
i. Nail roof decking at 4 in. o.c. along the edges and 6 in. o.c. in the field.
ii. Install a 4-in.-wide (nominal) ASTM D1970 compliant self-adhering polymer-modified bitumen or AAMA 711-13, Level 3 roof deck flashing tape over all roof horizontal and vertical roof deck seams, then cover the deck with a #30 felt or an equivalent synthetic underlayment. Lap up the side walls 4–6 in., and tape with flashing tape. Fasten underlayment with button cap nails at 6 in. o.c. along the laps and 12 in. o.c. spacing, vertically and horizontally, between the laps
iii. Install a two-layer #30 felt underlayment. To achieve a double layer, cut 17 in. off one side of the roll, and install the remaining 19-in.-wide strip of underlayment. Tack in place. Install a 36-in.-wide roll of underlayment over the 19-in.-wide course of underlayment along the eave. Continue, overlapping the sheets 19 in. (leaving a 17-in. exposure). Attach underlayment with button cap nails at 6 in. o.c. along the laps and 12 in. o.c. spacing, vertically and horizontally, between the laps. Lap up the sidewalls 4–6 in., and tape with flashing tape.
iv. Install a self-adhered (peel-and-stick) membrane meeting ASTM D1970 requirements over the entire roof deck. Lap up the sidewalls 4–6 in.
v. Fasten underlayment with button cap nails at 6 in. o.c. along the laps and 12 in. o.c. spacing, vertically and horizontally, between the laps.
i. High-Wind Roof Covering
i. Asphalt shingles should be high-wind rated and be installed with six nails, per high-wind installation instructions.
ii. For shingle roof installations, seal the drip edge at eaves using a self-adhering starter strip or applying an 8-in.-wide layer of flashing cement, maximum 1/8 in. thick.
iii. Use asphalt roof cement to glue and ensure bonding to enhance the attachment of hip and ridge shingles.
iv. Roof coverings (metal, concrete and clay tile, low-sloped roofs, wood shakes, or shingles) installed per manufacturer instructions for the site-specific wind speed and design pressures.
v. Install drip edge on top of the underlayment (except where instructions or the building code stipulate a different method), extend a minimum of 1/4 in. below roof sheathing, and extend onto the roof deck 2 in.
vi. Drip edges must be mechanically fastened to the roof deck at a maximum of 4 in. o.c.
vii. Install flashing at wall and roof intersections at each change in roof slope or direction and around roof openings. A flashing shall be installed to divert the water away from where a roof intersects a vertical sidewall.
viii. Base flashing against a vertical sidewall is continuous or step flashing, not less than 4 in. in height and 4 in. in width, and direct water away from the vertical sidewall onto the roof or into the gutter.
j. Continuous Load Path
i. Attach adjacent wood structural panel wall sheathing over common framing to provide lateral and uplift load continuity.
ii. Install all structural members per licensed engineer-designed load path.
iii. Increase the nailing to 4 in. at panel edges and 6 in. along intermediate supports (from a 6/12-in. pattern), and use ring/screw shank nails to increase withdrawal strength.
iv. Brace gable end walls at both the top and bottom, and ensure that they are properly attached to the roof and wall, respectively.
v. Sheathe all gable ends with wood structural panels that have the same performance category as the walls.
vi. Attach roof framing member to the wall top plates with a fastener that resists loads in all three directions.
vii. Ensure that trusses and rafters, especially those with taller heels, are properly braced with solid blocking between the top plates and roof sheathing to transfer the loads from the roof to the walls.
viii. Ensure that upper and lower floors are properly attached to resist uplift loads and create a solid lateral connection
ix. Attach sill plates to the foundation with 1/2 in. anchor bolts at 32-48 in. o.c. Provide a 3x3-in.-square plate washer at each anchor bolt. Ensure that the wall sheathing is attached to the properly anchored sill plate with the nailing pattern on the edge of the sheathing, as required by the wall design.
k. Garage Doors
i. Install additional brackets and rails in the garage door. Brackets reinforce the frame, and the rails reinforce the garage door.
ii. For garage doors without glazed openings (windows), install garage door assembly to meet design wind pressure for the site, or install protection for the garage door.
iii. For garage doors with glazed openings (windows), install garage door assembly to meet design wind pressure and impact for the site, or install protection for the garage door.
l. Wall System
i. Use a full wrap of OSB or plywood around the exterior of the home, running from roof to foundation. Nail per IRC 6 in. o.c. on all four edges and 12 in. o.c. in field.
ii. Increase interior and exterior shear walls nailing pattern to 4 in. o.c. on edges and 6 in. o.c. in field.
iii. Inspect nailing patterns for exterior structural panels and shear walls.
iv. Anchor corrugated brick ties into studs, not sheathing, OR anchor into sheathing according to IRC 2018 Table 703.8.4(2).
v. Install reinforced CMU/ICF for exterior walls of the home, running from roof to foundation, including foundation/basement walls, if present.
vi. Do not install fiber cement exterior cladding with blind nailing.
m. Soffit
i. Install additional nailing strips for all types of soffit materials.
ii. Follow manufacturer-recommended high-wind application for vinyl and metal soffit.
iii. Confirm nailing patterns of fiber cement or wood soffit material.
iv. Apply fiber cement soffit material over additional nailing strips.
n. Pressurization Design
i. Install structural framing to stack openings of each level, as indicated by construction documents.
ii. Install shear walls to have a low aspect ratio (height-to-width), as indicated by construction documents.
iii. Install shear walls/protections at corners, as indicated by construction documents.
iv. Install walls per engineer-optimized lengths, as indicated by construction documents.
v. Install larger openings parallel to main roof joists in non-load-bearing walls, as indicated by construction documents.
o. Chimney
i. Masonry chimney adjacent to the building envelope should be properly reinforced and anchored back to the wood framing.
ii. Chimney must be less than 5 ft. unless engineered.
iii. Masonry chimney sitting on top of a deck and that penetrates the balloon frame should be properly reinforced and engineered.
iv. Framed chimneys that penetrate roof structure around metal flue on top of roof should be properly anchored, balloon framed, and engineered.
v. Framed chimneys adjacent to the building envelope around metal flue should be properly anchored and attached to the structure.
p. Roof-Mounted Equipment
i. Ground-mount solar PV panels.
ii. Solar (photovoltaic [PV]) should be installed at “zero tilt.” Attachment to roof should not compromise roof system and should be engineered per site location with proper flashing.
iii. Ground-mount exterior HVAC equipment.
iv. Ground-mount deck.
v. Deck attachments to roof should not compromise roof system and should be engineered per site location with proper flashing.
10. Criterion 3.10: Resilient Site Design - Flood		Comment by Customization Instructions: Retain if Criterion 3.10 is selected to earn optional points. Retain only the Option selected by the project team. Projects located in Special Flood hazard Areas, that have experience repetitive loss, or severe repetitive loss are not eligible to earn points under this Criterion. 	Comment by Customization Instructions: NYC Overlay: Criterion 3.10 is required.
Option 1: ASCE 24-24 Compliance
a. Lowest floor of all buildings is elevated to at least Design Flood Elevation (DFE) + freeboard elevation, as required by ASCE 24-24 and ASCE 7-22 Supplement 2 for the occupancy category.
b. Install dry floodproofing only where allowed by ASCE 24-24 and ASCE 7-22 Supplement 2.
c. Utility systems and equipment are located and installed per ASCE 24-24 and ASCE 7-22 Supplement 2.
Option 2: HUD One-Pagers for Water	Comment by Customization Instructions: Retain only the specifications below which are applicable based on selected HUD strategies (all strategies under Connectors and Fasteners are required if Option 2 is chosen).
d. Wall Assembly
i. Spray studs with borate treatment to a minimum of 4 ft. or 12 in. above base flood elevation (BFE) in field (all first floor and floor joists, if applicable).
ii. Block and use galvanized screws to attach non-paper-faced gypsum at least 4 ft. above BFE on all first floor walls.
iii. Install all wall insulation on exterior of frame. Do not install cavity insulation.
iv. For wood and cement-based siding, fur out siding for better cladding drainage. Allow for back venting at top and bottom of cladded wall.
v. When using vinyl- and cement-based cladding systems, install a solid sheathing, such as oriented strand board (OSB), behind the drainage plane material.
e. Utilities and Mechanical Equipment
i. Install backflow valves on the sanitary sewer lateral or the internal plumbing branch serving below grade fixtures.
ii. Install quick-connect mechanisms on equipment essential to a building utility system, allowing for fast replacement of components, where allowed by code.
iii. Install HVAC equipment and electrical panel box above the 0.2-percent-annual-chance (or 500-year) flood elevation or higher. 
iv. Install all electrical systems, equipment, and components; heating, ventilating, air-conditioning; plumbing appliances and plumbing fixtures; duct systems; and other service equipment above the BFE.
f. Freeboard Elevation
i. Coastal Zone A: Install top of lowest floor one foot above the BFE. Coastal Zone V: Install bottom of lowest horizontal structural member above the BFE.
ii. Install bottom of lowest horizontal structural member 2 feet above the BFE, or above the 500-year flood elevation (whichever is greater).
iii. Install bottom of lowest horizontal structural member 4 feet above the BFE.
g. Install all connections so that they can be inspected and are accessible for corrosion inspection and replacement.
Option 3: Floodproofing of Critical Services
h. At least one exit door is installed above design flood elevation (DFE).
i. All central space-heating and water-heating equipment (if present) installed above DFE.
j. Install service disconnect at a readily accessible location above the DFE.
11. Criterion 3.11: Resilient Site Design: Wildfire		Comment by Customization Instructions: Retain if Criterion 3.11 is selected to earn optional points:
 a. and b. apply for all projects
 c. through g. apply only for projects earning 12 points
a. All vegetation, combustible fencing, or other flammable item removed from ignition zone 0 (0 - 5ft from each building).
b. Roof eaves are constructed with soffit closings (i.e., closed eaves or box eaves).
c. Shrubs planted in ignition zone 1 (5 - 30ft from each building) are spaced to resist spread of fire. 
d. Vegetation planted within 5-30 feet of each building (ignition zone 1) is fire-resistant/high-moisture.
e. Mow grass to a low height.
f. Cover all vents with 1/8-inch metal mesh.
g. Enclose under-deck areas with metal screening.
Water
12. Criterion 4.1: Water-Conserving Fixtures		Comment by Customization Instructions: Delete if Criterion 4.2, Option 2: Whole-home water certification is selected to earn optional points.
a. Installed service pressure does not exceed 60 PSI (excluding piping for fire sprinkler systems) and is controlled by a pressure regulator if necessary.
13. Criterion 4.2: Advanced Water Conservation	Comment by Customization Instructions: Delete if Criterion 4.2, Option 2: Whole-home water certification is not selected to earn optional points.	Comment by Customization Instructions: NYC Overlay: Criterion 4.2, Option 1 or 2, is required.
a. Install all plumbing and water fixtures to meet requirements of whole-home WaterSense certification.
14. Criterion 4.3 Water Quality	
a. Replace all lead service lines, ensuring replacement extends from water main to building's main interior shut-off valve. Replace the line before or while replacing the associated water heater(s). Document all completed replacements via inspection reports, photographs, or confirmation from the licensed plumber or utility responsible for the replacement.	Comment by Customization Instructions: Retain if project is:
Substantial Rehab constructed before 1986
Substantial Rehab constructed in 1986 or later, and this requirement is selected for optional points.
Moderate Rehab, and this requirement is selected for optional points.
b. If nitrate remediation is required (test results show > 50 mg/L nitrates or > 11 mg/L for nitrogen):	Comment by Customization Instructions: Retain if project selects Water Testing and Remediation to earn optional points, and testing for nitrates is selected. 
If water testing and remediation is selected to earn optional points and the project is served by a private well, this specification is required. 
If the project is on a public water supply and the building was constructed before 2014, this specification is highly recommended.
i. Install custom or pre-engineered reverse-osmosis or ion-exchange water treatment system.
15. Criterion 4.4: Monitoring Water Consumption and Leaks		Comment by Customization Instructions: Retain if Criterion 4.4 is selected to earn optional points. Retain only the Option(s) applicable and selected by the project team. If Criterion 4.4 is selected, specification a. is always required.
a. Before project completion, conduct pressure-loss test and visual inspection of every accessible, visible water supply connection and valve for water-using fixtures, appliances, and equipment. Fix any leaks detected during inspection.
Option 2: Pre-Rehabilitation Leak Assessment
b. Prior to construction start, inspect 100% of common areas and 10 dwelling units (or 20% of units, whichever is greater) for:
i. Toilet leaks (dye/tab test or continuous-run check)
ii. Dripping faucets/showerheads and stuck mixing valves
iii. Visible leaks at hose bibbs, clothes washers, ice makers, and water-heater relief valves.
c. Perform one of the following:	Comment by Customization Instructions: Retain only the option selected by the project team.
i. Prior to construction start, conduct pressure decay or districted shut-off testing on domestic mains/risers. Identify and document zones with losses.
ii. Prior to construction start, conduct acoustic/ultrasonic survey of mains/risers/recirculation loops. Document survey results.
iii. Prior to construction start, conduct thermal scan of domestic hot water recirculation. Identify and document unintended cross-flows or failed check valves.
d. Prior to construction start, test DHW return temperature and verify recirculation pump operation according to expected pump hot water delivery schedule and performance per design.	Comment by Customization Instructions: Retain if building has a central DHW recirculation loop.
e. Prior to construction start, test makeup-water meter.  	Comment by Customization Instructions: Retain if building has cooling towers.
f. During construction, if domestic hot water remains active, maintain temporary leak monitoring (interval meter, smart valve, or daily reads) and weekly walk-downs of wet rooms and mechanical spaces. Record and address new leaks discovered during selective demolition
Option 3: Advanced Water Metering
g. Water meters are installed to separately meter the following end uses:	Comment by Customization Instructions: Retain end uses selected by project team.
i. Each cold-water branch off the apartment line serving individual dwelling units
ii. Each cold-water riser and domestic hot water cold-water feed for all buildings in the project
iii. Common laundry facilities
iv. All toilets (both in dwelling unit and in common areas)
v. Boiler makeup water
vi. Outdoor water consumption
vii. Water consumption in any nonresidential spaces within buildings
16. Criterion 4.5: Efficient Plumbing Layout and Design		Comment by Customization Instructions: Retain if Criterion 4.5 is selected to earn optional points. Retain only the Option (and Strategy, for Option 3) selected by the project team.	Comment by Customization Instructions: NYC Overlay: Criterion 4.5 is required.
Option 1: Performance design path
a. Install plumbing system piping in accordance with IAPMO Water Demand calculations or 224 UPC Appendix M, per construction documents.
Option 3: Volumetric Design path
b. Strategy A: Conduct testing of hot water fixtures to verify no more than 0.5 gallons of water in any piping/manifold between the fixture and the hot water source. To account for the additional water that must be removed from the system before hot water can be delivered, no more than 0.6 gallons of water shall be collected from the fixture before a 10°F rise in temperature is observed.
c. Strategy B: Conduct testing of hot water fixtures to verify no more than 1.8 gallons of water in any piping/manifold between the fixture and the hot water source. No more than 1.8 gallons of water shall be collected from the fixture before a 10°F rise in temperature is observed.
The hot water source is considered to be either the in-dwelling hot water heater, the loop of the central hot water system, or the riser pipe from the central hot water system.
17. Criterion 4.7: Access to Potable Water During Emergencies		Comment by Customization Instructions: Retain if Criterion 4.7, Options 1: Pressurized water supply or 3: On-site well, are selected to earn optional points. Retain only the option selected by the project team.	Comment by Customization Instructions: NYC Overlay: Delete this Criterion
a. Option 1: Install fixtures that residents can use to fill water containers using only the available pressure from the water main. Access points must be located above design flood elevation, be ADA accessible, may not be located in restrooms, and must be accessible to all residents during a power loss.
b. Option 2: Install on-site drilled well or gravity-fed spring catchment.
Energy
18. Criterion 5.2a: Building Performance		Comment by Customization Instructions: Retain if project is:
New Construction
NOT using Criterion 5.3, Option 2
Select program based on building type.
a. Coordinate with a qualified third-party energy rater to certify each dwelling unit under the ENERGY STAR Multifamily New Construction program.
19. Criterion 5.2b: Building Performance		Comment by Customization Instructions: Retain if project is:
Substantial Rehab
Moderate Rehab
NOT using Criterion 5.3, Option 2
Retain only the option selected by the project team.
a. Option 1: Energy Rating Index: Install energy efficiency measures in accordance with the final design energy model, which demonstrates that each dwelling unit achieves an ERI score of [80 / 90] or less. Verify all measures using a qualified third-party energy rater per ANSI/RESNET/ICC 301.	Comment by Customization Instructions: Select ERI target based on project type:
Moderate rehab pre-1980: 90
Substantial rehab or moderate rehab post-1980: 80
b. Option 2: ASHRAE 90.1: Install energy efficiency measures in accordance with the final design energy model, which demonstrates compliance with ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016. 
c. Option 2: Project in California: Install energy efficiency measures in accordance with the final design energy model, which demonstrates compliance with the version of Title 24 under which the project is permitted.
d. Projects using Energy Outreach Colorado Program: Install energy efficiency measures in accordance with the final design energy model, which demonstrates compliance with the Energy Outreach Colorado program.
e. Complete and pass testing via the ENERGY STAR National HVAC Functional Testing Checklist, Version 1.1. 100% of existing systems must be tested and a subset of new systems may be tested according to the sampling policy contained in the checklist.
f. Use HVAC load calculation software programs reviewed by ACCA to perform Manual J and S calculations for all new HVAC equipment.
g. Select and install HVAC equipment according to ACCA Manual J and S procedures to ensure right-sizing for all new HVAC equipment.
h. Install thermal insulation to Grade 1 level per ANSI/RESNET/ICC Standard 301. Grade II level permitted in floors if they fill full width and depth, as long as R-value of the batts has been appropriately assessed based on manufacturer guidance and the only defect preventing the insulation from achieving Grade I is the compression caused by the excess insulation. Insulation installation grade must be verified by a qualified third-party energy rater.	Comment by Customization Instructions: Delete if rehab scope does not include insulation.
i. Perform air infiltration tests for at least 10% of dwelling units in the building across a variety of unit types and install air sealing measures required to achieve [0.30 / 0.40] CFM50/sfbe in each dwelling unit.	Comment by Customization Instructions: Select infiltration target based on project type:
Substantial rehab without a historic designation: 0.30
Moderate rehab or substantial rehab with a historic designation: 0.40
j. Perform pre-retrofit air infiltration tests for at least 5% of dwelling units in the building across a variety of unit types, and post-retrofit tests for at least 10% of dwelling units. Install air sealing measures required to achieve 20% improvement between the two tests.	Comment by Customization Instructions: Retain if project is a moderate rehab or a substantial rehab with a historic designation.
i. Projects may use one or a combination of these two targets for different dwelling units.
k. NYC Overlay: Install energy efficiency measures in accordance with requirements of the New York City Prescriptive Pathway for Tenant in Place Rehabs.	Comment by Customization Instructions: NYC Overlay: Eligible projects may comply with this mandatory criterion by following the NYC Prescriptive Pathway for Tenant in Place Rehabs. If this option is selected, delete all other specifications under this Criterion.
20. Criterion 5.3: Advanced Building Performance		Comment by Customization Instructions: Retain if Criterion 5.3 is selected for points. Retain only the option selected by the project team.
If Option 2 is selected, delete Criterion 5.2a/b above.
a. Option 1: Performance Above Mandatory Requirement (New Construction): Install energy efficiency measures in accordance with the final design energy model. Coordinate with a qualified Rater per ANSI/RESNET/ICC 301 to verify that each dwelling unit achieves an ERI score at least 5 points more efficient than ENERGY STAR Multifamily New Construction program's ERI Target Score, or is at least 5% more efficient than the program's ASHRAE target.
b. Option 1: Performance Above Mandatory Requirement (Rehabilitation, ERI Path): Install energy efficiency measures in accordance with the final design energy model. Coordinate with a qualified energy rater per ANSI/RESNET/ICC 301 to verify that each dwelling unit achieves an ERI score of [75 / 85] or less.	Comment by Customization Instructions: Select ERI target based on project type:
Substantial rehab with no historic designation: 75
Moderate rehab or substantial rehab with historic designation: 85
c. Option 1: Performance Above Mandatory Requirement (Rehabilitation, ASHRAE Path): Install energy efficiency measures in accordance with the final design energy model, which demonstrates at least 5% savings beyond ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016, excluding on-site power generation.
d. Option 1: Performance Above Mandatory Requirement (Rehabilitation, Title 24 Path): Install energy efficiency measures in accordance with the final design energy model, which demonstrates at least 5% savings beyond the version of Title 24 under which the project is permitted.
e. Option 2: Advanced Building Certification (DOE Efficient New Homes): Coordinate with a qualified third-party energy rater to certify each dwelling unit under the DOE Efficient New Homes program for the program version applicable based on project type and permit date.
f. Option 2: Advanced Building Certification (ENERGY STAR NextGen): Coordinate with a qualified third-party energy rater to certify each dwelling unit under the ENERGY STAR NextGen program.
g. Option 2: Advanced Building Certification (Passive House International): Coordinate with a qualified third-party energy rater to certify each dwelling unit under the Passive House International Classic, Plus, Premium, LEB, or EnerPHit program.
h. Option 2: Advanced Building Certification (Phius): Coordinate with a qualified third-party energy rater to certify each dwelling unit under the Phius CORE, ZERO, or REVIVE program.
i. Option 3: Deep Energy Retrofit (Rehabilitation, ERI Path): Install energy efficiency measures in accordance with the final design energy model. Coordinate with a qualified energy rater to verify that each dwelling unit achieves an ERI score of [65 / 75] or less.	Comment by Customization Instructions: Select ERI target based on project type:
Substantial rehabs: 65
Moderate rehab: 75
j. Option 3: Deep Energy Retrofit (Rehabilitation, ASHRAE Path): Install energy efficiency measures in accordance with the final design energy model. Coordinate with a qualified energy rater to verify that the building's energy performance achieves at least [10% / 15%] savings beyond ASHRAE Standard 90.1-2013, according to the methodology in Appendix G 90.1-2016, excluding on-site power generation.	Comment by Customization Instructions: Select target based on project type:
Substantial rehabs: 15%
Moderate rehabs: 10%
k. Option 3: Deep Energy Retrofit (Rehabilitation, Title 24 Path): Install energy efficiency measures in accordance with the final design energy model. Coordinate with a qualified energy rater to verify that the project's energy performance is at least [10% / 15%] better than the version of Title 24 under which the project is permitted.	Comment by Customization Instructions: Select target based on project type:
Substantial rehabs: 15%
Moderate rehabs: 10%
21. Criterion 5.4: All -Electric and Electric-Ready Design		Comment by Customization Instructions: Retain if project is:
New Construction, and all-electric project is not selected for points.
Rehab, and Criterion 5.4b, Option 1 is selected to earn optional points.	Comment by Customization Instructions: NYC Overlay: New construction projects are required to be all-electric. Rehabs have a third option to earn optional points under this Criterion: electric space heating and cooling. If this option is selected, no Execution requirements apply under this Criterion.
a. Install branch circuits within 3 feet of gas or propane space heating appliances in dwelling units with no obstructions. Circuits must be dedicated to future electric replacement equipment (125V, 20amp) and cannot be used for other appliances.	Comment by Customization Instructions: Retain a. through c. if project contains non-electric, in-dwelling space heating.
b. Dedicate space in the electric panel next to the space heating breaker for future conversion to 240V and label it as "240 Ready."
c. Include receptacles for future heat pumps to be connected to the panel with a 120/240V, 3-conductor, 10AWG copper wire, with both ends of the unused conductor labeled. Ensure these are electrically isolated.
d. Install branch circuits within 3 feet of gas or propane water heating appliances in dwelling units with no obstructions. Circuits must be dedicated to future electric replacement equipment (125V, 20amp) and cannot be used for other appliances.	Comment by Customization Instructions: Retain d. through f. if project contains non-electric, in-dwelling water heating.
e. Dedicate space in the electric panel next to the water heating breaker for future conversion to 240V and label it as "240 Ready."
f. Include receptacles for future electric water heaters to be connected to the panel with a 120/240V, 3-conductor, 10AWG copper wire, with both ends of the unused conductor labeled. Ensure these are electrically isolated.
g. Install a floor drain to accommodate condensate line near the receptacle for the future electric water heater. 	Comment by Customization Instructions: Retain g. and h. if project contains non-electric, in-dwelling water heating using a storage water heater (not tankless).
h. Provide approximately 3 feet by 3 feet of clear floor space with clearance height of at least 6 feet near the receptacle for the future electric water heater.
22. Criterion 5.6: Backup Power		Comment by Customization Instructions: Retain if Criterion 5.6, Option 3: Generator, or NYC Overlay: Shelter in Place Area option, is selected to earn optional points.
a. Connections are installed at the exterior of a building which will be accessible to connect to a generator when the electric grid goes down.
b. Backup generator systems undergo regular fuel testing in accordance with NFPA 110.
c. NYC Overlay: Provide Shelter in Place Area(s), sized per construction documents to equal 15 sf per bedroom. Wire each area to backup power. In each area, include:	Comment by Customization Instructions: NYC Overlay: This additional option to comply with Criterion 5.6 is only available to projects using the NYC Overlay.
i. Backup power for heating, cooling lighting, outlets, and WiFi
ii. Operable windows
iii. At least one accessible bathroom with potable water source
iv. Refrigerator space totaling at least 0.25 cubic feet per bedroom
23. Criterion 5.7: Renewable Energy		Comment by Customization Instructions: Retain if Criterion 5.7, Option 1, Strategy A. B, or D is selected to earn optional points.
a. PV installed on rooftops, parking lots, side lots, canopies, or garages. Total installed area equals at least 50% of the usable roof area.
24. Criterion 5.8: Electric Vehicle Charging	
a. Wire and install a Level 2 EVSE for at least one parking space on the site.	Comment by Customization Instructions: Retain a. and b. if project is new construction or substantial rehab, and is not using Criterion 5.8 to earn optional points.
b. If project has 20 or more parking spaces, install EV capable, EV ready, or Level 2 EVSE in at least 10% of parking spaces.
c. Install an Automatic Load Management System (ALMS) with sufficient capacity to deliver at least 3.3 kW simultaneously to each EV charging station that will be served by the ALMS. The branch circuit for the ALMS must have a minimum capacity of 40 amperes.	Comment by Customization Instructions: Retain if project uses ALMS.
d. Install as many EV-capable, EV-ready, and/or EVSE spaces as can be accommodated within the project's current electrical service capacity.	Comment by Customization Instructions: Retain if project is new construction and using the transformer exception.
e. Install as many EV-capable, EV-ready, and/or EVSE spaces as can be accommodated within the project's current electrical service capacity or the project's upgraded service capacity, after capacity is diverted to electrifying other end uses.	Comment by Customization Instructions: Retain if the project is substantial rehab and using the service upgrade exception.
f. Install Level 2 EVSE in at least 5% of the total number of parking spaces on the site.	Comment by Customization Instructions: Retain if project is using this specification to earn optional points. If used, delete all other specifications under this Criterion (except ALMS, if used).
g. Install Level 2 EV-capable, EV-ready, or EVSE spaces in more than 50% of the total number of spaces on the site.	Comment by Customization Instructions: Retain if project is using this specification to earn optional points. If used, delete all other specifications under this Criterion (except ALMS, if used).
h. NYC Overlay: For projects with 1-39 parking spaces, install at least two Level 2 EVSE.	Comment by Customization Instructions: NYC Overlay: Retain h. or i. if project is using this specification to earn optional points. These options are only available to projects using the NYC Overlay. If used, delete all other specifications under this Criterion (except ALMS, if used).
i. NYC Overlay: Provide Level 2 EV-capable or EV-ready spaces in more than 20% of the total number of spaces on the site.
For EV-capable spaces, provide electrical capacity and install conduit to support a Level 2 EV charger. EV-capable spaces are not required to have wiring or an outlet.
For EV-ready spaces, install all components (including wiring and outlets) required to support a Level 2 EV charger. EV-ready spaces are not required to include a charger.
25. Criterion 5.9: Passive Survivability		Comment by Customization Instructions: Retain if Criterion 5.9 is selected to earn optional points. Retain only the Option/strategy selected by the project team.
a. Option 1 - Natural Ventilation: Install at least one window in each dwelling unit that is operable and equipped with an insect screen.
b. Option 1 - Shading: Install measures that shade at least [95% / 75% / 50%] of south-facing windows by June 21, as specified in construction documents.	Comment by Customization Instructions: Select percentage based on Climate Zone:
CZ 1, 2: 95%
CZ 3, 4A, 4B: 75%
CZ 4C-8: 50%
i. Measures may include interior insulated window shades with a full-perimeter track, or exterior architectural features/overhangs and/or attachments (fins, shutters, blinds, awnings).
c. Option 2: Install all measures used in final thermal model.
Materials
26. Criterion 6.2: Reduction of Materials and Waste		Comment by Customization Instructions: Retain only the strategies selected to comply with mandatory requirements or to earn optional points.
a. Strategy A: Install concrete or steel according to the plan or diagram illustrating areas of the building optimized to reduce the amount used.
b. Strategy C: Install three standard products according to the design based on the product's dimensions in order to reduce waste to less than 5% of the material used. Use the following three products:
i. [insert product category / Contractor may select three products.]
c. Strategy D: Install at least 50% of the square footage of all buildings in the project with industrialized modular construction methods, integrating off-site, prefabricated volumetric, or panelized manufacturing.
d. Strategy E: Install salvaged materials for 15% of the following product type:
i. [insert product category / Contractor may select product type.]
e. Strategy F: Conduct a pre-demolition salvage assessment. Identify building materials, soils, and landscaping to be removed. Create and follow a plan to divert at least 35% from landfill.
f. Strategy G: Create and follow a waste-management plan for use during construction that diverts at least 50% of construction waste by weight from landfill.
g. Strategy H: Recycle all waste generated on the site for at least two of the following product waste types: cardboard, wood, drywall, metals, concrete, brick, asphalt, insulation, carpet, plastics.
h. Strategy I: Create end-of-use guidance for five product categories, identifying products, locations in the building, installed quantities, anticipated life spans, and recommended actions to salvage them or recover them for recycling. Include information for specific organizations or businesses that will assist with end of use. Train the building manager to enact this guidance.
i. Strategy J: Train the building manager on any installed products with extended producer responsibility programs (e.g., take-back programs). 
j. Strategy K: Create guidance for three assemblies in the building that are designed for disassembly.
k. Strategy L: Create guidance on disassembly methods for installed modular construction elements.
27. Criterion 6.3: Reduction of Lead Hazards in Pre-1978 Buildings		Comment by Customization Instructions: Retain if project is a substantial rehab constructed before 1978. Retain only the option selected by the project team. Specification a. is required for all projects using this Criterion.
a. Ensure that the people testing and remediating lead understand and adhere to lead-safe work practices to minimize and contain dust.
b. Option 1: Conduct a lead risk assessment or inspection to identify lead hazards. Control identified lead hazards using lead abatement or interim controls. Follow U.S. Environmental Protection Agency (EPA) and state and/or local laws and requirements, where applicable. Check state or local regulations for additional requirements for lead-safe work pertaining to prohibited practices, notification, worker training and certification, and clearance dust training.
c. Option 2: Follow standard lead treatments defined by HUD as a series of hazard-reduction measures designed to reduce all lead-based paint hazards in a dwelling unit.
28. Criterion 6.4: Advanced Material Selection		Comment by Customization Instructions: Retain all mandatory requirements and strategies selected to earn optional points.
a. Flooring
Option 2: Minimum Flooring Standards
i. No carpet is installed in building entryways, laundry rooms, bathrooms, kitchens/ kitchenettes, or utility rooms. Walk-off mats manufactured especially for that purpose are acceptable at entryways.
ii. No flexible PVC with phthalates is installed (in either vinyl flooring or carpet backings).
iii. No rubber or rubber–cork flooring made with tire-derived crumb rubber is installed.
iv. No carpet with intentionally added PFAS stain-repellant treatments is installed.
v. Fluid-applied finish floors are only installed in spaces that are not regularly occupied, such as mechanical rooms.
For additional points:
vi. No carpet is installed anywhere in the project.	Comment by Customization Instructions: If this specification is selected to earn optional points, items i. and iv. (above) can be deleted.
vii. No vinyl flooring is installed anywhere in the project.
b. Insulation
Options 1 or 3: 
i. Two-part spray polyurethane foam is installed in limited scope to establish a sealed air barrier. It is only used if no other viable material options are available.
c. Do not install any wall coverings that contain vinyl.
29. Criterion 6.5: Recycling Storage		Comment by Customization Instructions: Retain if Criterion 6.5 is selected to earn optional points, and municipal recycling services are available to the building.	Comment by Customization Instructions: NYC Overlay: All projects required to comply with Criterion 6.5. In addition to trash and recycling bins, projects must provide dedicated organics (compost) collection in all waste storage areas, with containers sized and configured to meet DSNY organics-storage requirements.
a. Provide separate bins for the collection of trash and recycling in each dwelling unit.
b. Provide separate bins for the collection of trash and recycling in all shared community rooms.
c. On each floor, provide room for separate bins for trash and recycling or install separate trash and recycling chutes.
d. Provide clear signage and labeling to distinguish recycling bins from general trash bins at all communal recycling and trash sites.
Healthy Living Environment
30. Criterion 7.1: Clean Air - Radon Testing and Mitigation		Comment by Customization Instructions: Retain if project is located in Radon Zone 1, and either new construction or substantial rehab. Retain only the specifications applicable based on project type.
New Construction:
a. Install passive radon-resistant features below the slab as indicated by construction documents.
b. Install a vertical vent pipe with a junction box within 10 feet of an electrical outlet.
Substantial Rehab:
c. Conduct a pre-construction test for radon by a radon professional in accordance with ANSI-AARST MA-MFLB-2023. In time-sensitive situations, consistent with the U.S. Department of Housing and Urban Development’s (HUD) radon policy, a radon professional may sample a minimum of 25% of randomly selected ground-level dwelling units. If test results exceed 4 pCi/L (picocuries per liter), install radon-reduction measures outlined in ANSI-AARST SGM-MFLB-2023.
d. Conduct a post-construction test for radon by a radon professional in accordance with ANSI-AARST MA-MFLB-2023. If test results exceed 4 pCi/L (picocuries per liter) and exceed pre-construction test results, install radon-reduction measures outlined in ANSI-AARST SGM-MFLB-2023.
31. Criterion 7.2: Clean Air - Combustion Equipment		Comment by Customization Instructions: Retain if project has combustion equipment in conditioned space. Delete if combustion equipment is located only in detached utility buildings or nonenclosed spaces.
a. Install one hard-wired carbon monoxide (CO) alarm with battery backup function for each sleeping zone and placed per National Fire Protection Association (NFPA) 72.  
b. Conduct combustion safety testing prior to and after the retrofit for central systems and for 10% of individual dwelling-unit systems, using either: 	Comment by Customization Instructions: Retain if project is a substantial or moderate rehab and existing combustion equipment in conditioned space is not power- or direct-vented or scheduled for replacement.
i. RESNET Standard for Combustion Safety Testing and Work Scope
ii. BPI Combustion Appliance and Fuel Distribution System Inspection
iii.  (California only) Multifamily Home Energy Retrofit Coordinating Committee (MF HERCC) Combustion Safety Testing Protocols for Existing Multifamily Buildings.
Report any deficiencies immediately to the owner or owner’s representative if any system fails testing.
32. Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
a. Install visible signage in parking and drop-off areas prohibiting vehicles on the property from idling longer than two minutes.
b. Install a continuous air barrier between conditioned space and any garage space.	Comment by Customization Instructions: Retain b. through e. if project includes a garage for vehicle parking.
i. Seal between all walls separating conditioned and garage spaces with foam and/or caulk.
ii. Seal all pipe and conduit penetrations with material compatible with the adjacent materials and resilient to temperature fluctuations and providing fire-resistive characteristics if required by authorities having jurisdictions.
iii. Block and seal floor trusses and joists between conditioned space and garage with foam and/or caulk.
c. Visually inspect all common walls and ceilings between attached garages and conditioned spaces to ensure they are air-sealed before insulation is installed.
d. HVAC systems for garages are completely separate from HVAC systems serving conditioned interior spaces. Do not install ductwork or air-handling equipment for conditioned interior spaces in a garage.
e. Fit all connecting doors between conditioned space and garages with gaskets or make these doorways substantially airtight with weather stripping and airtight door sweeps.
f. Install one hard-wired carbon monoxide (CO) alarm with battery backup function for each sleeping zone and placed per National Fire Protection Association (NFPA) 72.  	Comment by Customization Instructions: Delete if project:
Does not have a parking garage
Has a mechanically vented garage
Only has open parking structures
33. Criterion 7.5: Clean Air - Ventilation		Comment by Customization Instructions: Retain if project is:
New construction 
Substantial rehab
Moderate rehab, and Criterion 7.5 is selected to earn optional points. For Moderate rehabs, retain only the options selected to earn points by the project team.
a. Install in-unit kitchen mechanical exhaust system(s) in accordance with ASHRAE 62.2-2022, sections 5 and 7 and manufacturer's recommendations.
i. Or, if no combustion-fueled appliances are located within the dwelling unit, install heat- or energy-recovery ventilator or a ceiling- or wall-mounted fan exhausting kitchen air to the outdoors, in accordance with the manufacturer's recommendations.	Comment by Customization Instructions: Retain if Criterion 5.3, Option 2: Advanced building certification is selected to earn optional points.
b. Install bathroom mechanical exhaust system(s) in accordance with ASHRAE 62.2-2022, sections 5 and 7 and manufacturer's recommendations. If bath fans do not run continuously, install them with controls that ensure adequate run time.
c. Install whole-house mechanical ventilation system in accordance with ASHRAE 62.2-2022, sections 4 and 7 (excluding section 4.2) and manufacturer's recommendations.
d. Install mechanical ventilation system(s) serving hallways, stairwells, and common/amenity spaces in accordance with ASHRAE 62.1-2022 and manufacturer's recommendations.	Comment by Customization Instructions: Retain if project is four stories or more.
e. Install all mechanical exhaust ventilation systems to terminate outdoors. These systems may not terminate in attics or interstitial spaces.	Comment by Customization Instructions: Specifications e. and f. are required if this Criterion is used.
f. Install all dwelling-unit ventilation systems to operate as designed, with flow rates within +/- 15 CFM or +/- 15% of design value, whichever is smaller. Verify these flow rates.
g. Clean, seal, balance, and right-size rooftop fans for all existing central ventilation systems and associated ductwork.	Comment by Customization Instructions: Retain if project is substantial or moderate rehab.
34. Criterion 7.7: Clean Air - Enhanced IAQ		Comment by Customization Instructions: Retain if Criterion 7.7 is selected to earn optional points. Retain only the Option selected by the project team.	Comment by Customization Instructions: NYC Overlay: This Criterion is required, and may be met using Option 1 or Option 2.
Option 1: Management of construction pollution
a. In all dwelling units, seal all heating, cooling, and ventilation ducts and returns throughout construction to prevent dust, harmful particles, and other construction-related pollution from entering.
b. Flush all dwelling units after completion of construction and prior to occupancy, using one of the following methods: 
i. for at least 48 hours (may be nonconsecutive) with all windows and interior doors open and all HVAC fans running
ii. with at least 14,000 cubic feet/sf of floor area. 
For either method, replace all air-handling equipment filters after flushing.
		Option 2: Indoor AirPlus
c. All products meet the requirements of the EPA Indoor AirPlus program.
35. Criterion 7.8: Moisture - Dehumidification		Comment by Customization Instructions: Retain if project is:
Located in CZ 1A, 2A, 3A, or 4A, and has selected Criterion 5.3 to earn optional points. 
Located in any CZ, and selected Criterion 7.8 to earn optional points.
Retain only the Option selected by the project team.
a. Option 2: Dehumidification Readiness: In each dwelling unit, install a drain and electrical hook-up compatible with a supplemental dehumidification system. Provide a dedicated space adjacent to the drain and hook-up for a future supplemental dehumidification system.
b. Option 3: ERV or HRV	Comment by Customization Instructions: NYC Overlay: Option 3 is required for projects following Criterion 5.3.
i. Install an energy-recovery ventilator (ERV) or heat-recovery ventilator (HRV) that serves every dwelling unit.
ii. Conduct a condensation evaluation for window-to-wall connections and at any non-thermally-broken metal penetrations through the exterior envelope.
iii. Size cooling systems to ensure dehumidification capacity is maximized, given the expected loads in the apartments.
iv. Install relative humidity monitors in return-air ducts at the ERV or HRV.
36. Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction		Comment by Customization Instructions: Retain if project is new construction.
a. Install roof overhangs, gutters, downspouts, and/or other strategies to divert bulk water away from wall systems and onto a downward slope at least 5 feet from the foundation— or, if relying on underground catchment systems, at least 10 feet from the foundation.
b. Properly install weather barriers, including flashing and drainage planes, to help direct water away from wall cavities. 
c. Install flashing at the bottom of exterior walls, along with a continuous, fully sealed drainage plane behind exterior cladding that laps over the flashing. 
d. Include weep holes, weep screed, or an equivalent drainage system appropriate to the assembly type and materials.
e. Fully flash and lap all wall and roof penetrations, including windows and doors.
f. For projects with new concrete slab (for basements, crawl spaces, or slab on grade construction), install a capillary break as follows:	Comment by Customization Instructions: Projects on raised-pier foundations with no foundation walls can delete f. and g.
i. 4-inch layer of ½-inch diameter or greater clean aggregate OR a 4-inch uniform layer of sand overlain with a layer or strips of geotextile drainage matting installed according to the manufacturer’s instructions
ii. Immediately above the capillary break, install insulation as necessary.
iii. Above that, install at least 6-mil polyethylene sheeting overlapped at least 6 inches at the seams to serve as a vapor retarder in direct contact with the slab above."
g. For projects with crawl spaces that have no concrete slab, install a vapor retarder as follows:
i. Install at least 8mm cross-laminated polyethylene on the crawlspace floor, extended up at least 12 inches on piers and foundation walls, and with joints overlapping at least 12 inches. 
ii. Line the likely “high-traffic” areas of the crawl space with foam board so the polyethylene beneath will not be disturbed.
37. Criterion 7.9b: Managing Moisture in the Building Envelope - Rehabilitation		Comment by Customization Instructions: Retain if project is a substantial or moderate rehab.
a. Perform a property assessment, examining the interior and exterior of all [buildings / building assemblies] in the scope of work for evidence of moisture problems. Repair or remediate all moisture problems discovered.	Comment by Customization Instructions: Select based on project type:
Moderate rehabs: building assemblies
Substantial rehabs: buildings
The assessment should look for:
i. Water stains or wet spots
ii. Musty odors
iii. Foundation cracks and evidence of seepage
iv. Roof leaks
v. Plumbing leaks
vi. Condensation in attics, and in or around windows and doors
vii. Moisture damage near all envelope penetrations, including windows and doors; utility hookups; and mechanical, electrical, and plumbing systems
b. Provide a continuous housewrap/weather-resistive barrier on exterior walls, with sheets lapped shingle-style to prevent bulk water from penetrating the wall assembly or being introduced through window or door openings or through other penetrations. Alternatively, install a fluid-applied weather-resistive barrier in accordance with manufacturer instructions. Taped systems such as Zip, Force Field, and others are acceptable.
c. Prior to any exterior finish being installed, integrate flashings with the weather-resistive barrier and drainage plane to prevent bulk water from entering the exterior wall assembly. This must be done at roof–wall intersections and wall penetrations—including but not limited to plumbing, electrical, vents, and HVAC refrigerant lines in addition to windows and doors. Include kick-out flashing where a sloped-roof eave terminates in a wall with siding, stucco, or other applied finish apart from brick veneer.
d. For sloped roofs, install drip edge at the entire perimeter of the roof.
e. At roof–wall intersections, maintain a minimum 2-inch clearance (or other if recommended by the manufacturer) between wall cladding and roofing materials. Install flashing along the intersection and use kick-out flashing as noted above for wall systems.
38. Criterion 7.10 Managing Moisture: Bath, Kitchen, and Laundry Assemblies		Comment by Customization Instructions: Retain if project is:
New construction
Substantial rehab
Moderate rehab, and bathroom kitchen, and/or laundry is in scope. For Moderate rehabs, only retain items in this section which are applicable based on scope of work.
a. Install only approved materials behind tub and shower enclosures, as described in Part 2 - Products.
b. Throughout bathrooms, kitchens, and laundry rooms, install surface materials that are durable, cleanable, and are not prone to deterioration due to moisture intrusion.
39. Criterion 7.11: Reducing Allergens and Disease Vectors - Integrated Pest Management	
a. Seal all wall, floor, and joint penetrations with low-VOC caulking or other low-hazard sealing methods, such as screens, door sweeps, escutcheon plates, or elastomeric sealants, to prevent pest entry. 
b. Use rodent- and corrosion-proof screens (copper, stainless steel mesh, or rigid metal cloth) for openings greater than ¼ inch (about 2/3 centimeter). 
c. Thoroughly seal entry points under kitchen and bathroom sinks to prevent pest entry.
40. Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, New Construction		Comment by Customization Instructions: Retain if project is substantial or moderate rehab and Criterion 7.12b is selected to earn optional points. Retain only the Option(s) selected by the project team.
a. Option 1: Conduct a noise assessment and provide a site-specific noise-abatement plan that covers general noise mitigation techniques in accordance with U.S. Department of Housing and Urban Development (HUD) regulation 24 CFR Part 51, Subpart B.
b. Option 3: Interior Sources of Noise in Bedrooms
i. Grade A: Install and verify that bedroom party walls meet requirements of ICC G2-2010 Guideline for Acoustics, Grade A.
ii. Grade B: Install and verify that bedroom party walls meet requirements of ICC G2-2010 Guideline for Acoustics, Grade B.
41. Criterion 7.13: Personal and Social Safety		Comment by Customization Instructions: Retain if project is:
New Construction 
Substantial rehab
Retain only the strategies selected by the project team.
a. Strategy A: Construct public spaces to meet the following, in accordance with construction documents:
i. Avoid blind corners (using window slits, transparent materials, convex mirrors, or other design features at corners)
ii. Common-space paths wide enough for two people to comfortably pass. 
iii. No more than 20% of public spaces and common areas include blind corners for the path of travel."
b. Strategy B: Install “peephole” door viewers or dwelling-unit entry doors that include windows.
c. Strategy C: Locate dwelling unit entry doors to be staggered (across corridor or across walkways, in walk-up apartments), as specified in construction documents.
d. Strategy D: Provide secure, resident-controlled site access at all property entrances. Ensure gates and/or fences aside from the resident-controlled access point prevent direct entry to buildings from streets or adjacent lots.
e. Strategy E: 
i. Install at least one of: vegetated streets, vegetated walkways, landscaped fence lines or borders, or rain gardens, as indicated by construction documents.
ii. For all landscaped areas within 25 feet of a pedestrian path, building entry, playground, or parking area: 
a. keep shrubs and hedges trimmed to a maximum of 3 feet
b. trim tree canopies to a clearance height of 6 feet or more above ground level
f. Strategy F: Install at least two of the following: climate systems/thermostat; ceiling fans; shading devices; lighting that allows tuning, dimming, and/or switching between task, accent, and ambient conditions; adjustable vents.
g. Strategy G: Install locked storage for at least 50% of units. Storage is at least 10 square feet per dwelling unit, provided outside of the unit.
h. Strategy H: Install a drinking fountain or hydration station in at least one accessible common area.
i. Strategy I (more than 12 units): Install secure mailboxes and lockable package storage or lockers.
j. Strategy I (fewer than 12 units): Install lockable mailboxes.
42. Criterion 7.14: Social Connection and Accessibility - Design for All Ages/Abilities		Comment by Customization Instructions: Retain only the strategies selected by the project team to fulfill this mandatory requirement.
a. Strategy A: Install signage for wayfinding throughout the interior and exterior of the property.
b. Strategy B: Install floor finishes with subtle, neutral patterns and plain matte finishes in common spaces and at least 25% of dwelling units.
c. Strategy C: Mount light switches at 52 inches and power outlets at 20 inches above the finished floor.
d. Strategy D: Provide at least 3 seats in each common space using moveable furniture.
e. Strategy F: Install at least one restroom in common areas that meets universal accessibility requirements.
f. Strategy G: Install seating, toilets, drinking water, internet, and charging stations in interior common areas.
g. Strategy H: Install slip-resistant, hard-surface finishes in common spaces, hallways, entryways, and outdoor pathways.
h. Strategy I: Mount bathroom grab bars horizontally or vertically (not on the diagonal).
i. Strategy J: Install interior and exterior doors with no steps or raised thresholds. 
j. Strategy L: Install support (e.g., hand rails) on both sides of all sloped walking surfaces.
k. Strategy N: Install 36-inch rough opening for all doors.
l. Strategy O: Install permanent kitchen and bathroom cabinetry and sanitary appliances with enough clearance to provide a turning radius of at least 5 feet.
43. Criterion 7.15: Access to Nature and Biophilic Design		Comment by Customization Instructions: Retain if Criterion 7.15 is selected to earn optional points. Retain only specs selected by project team for points.
a. Install live plants, natural materials, or patterns that mimic nature in dwelling units as indicated by the project team.
b. Plant native and/or culturally significant vegetation that varies seasonally in usable outdoor spaces, as specified by the project team. 
c. Use hand or electric maintenance and no chemical herbicides in usable outdoor spaces.
d. Install raised beds, community gardens, or plantings with a variety of scents and textures, as indicated by the project team.
e. Plant or install flowering plants, bird baths, pollinator houses, bat houses, or perches, as indicated by the project team.
f. Install water features (fountains, rain chains, bioswales), as indicated by the project team.
44. Criterion 7.16: Healing-Centered and Culturally Responsive Design		Comment by Customization Instructions: Retain if Criterion 7.16 is selected to earn optional points. Retain only specs selected by project team for points.
a. Community-Generated Art: Install artwork in shared indoor or outdoor spaces, as specified by the project team. Ensure artwork is visible.
b. Storytelling Through Space: Install products and/or space labels per design and names selected by community members.
45. Criterion 7.17 Active Design: Promoting Physical Activity	
a. Install point-of-decision signage at building entrances and corridor intersections.	Comment by Customization Instructions: Retain a. through c. if Criterion 7.17, Option 1: Encouraging everyday stair use, is selected to earn optional points. Retain only specs selected by project team.

Buildings that include stairs as the only means to travel from one floor to another are not eligible for this option.
b. Install at least 10 square feet of transparent glazing at all stair doors from the corridor.
c. Install magnetic door holds on all doors leading to stairs from the corridor (as allowable by fire code).
d. Install adult exercise and/or children's play equipment in dedicated on-site recreation space.	Comment by Customization Instructions: Retain if Criterion 7.17, Option 2: Provide activity spaces, is selected to earn optional points. 
Operations, Maintenance, and Resident Engagement
46. Criterion 8.4: Walk-Throughs and Orientations to Property Operation	
a. Use materials provided under Criterion 8.1 and 8.2 to deliver training to facility management and building maintenance staff on all relevant systems. Share the list of Green Communities criteria that were implemented as part of the project. 
47. Criterion 8.5: Energy and Water Data Collection and Monitoring		Comment by Customization Instructions: Retain only the Option selected by the project team.	Comment by Customization Instructions: NYC Overlay: Two additional options are available under this Criterion for projects receiving HPD subsidy. See NYC Overlay checklist for details.
a. Data must be uploaded and tracked at least annually in an online utility benchmarking platform for at least five years after EITHER 1) issue of the certificate of occupancy for rehabs OR 2) lease-up for new construction. Viewing access must be granted to Enterprise for the required five-year period. 	Comment by Customization Instructions: Delete if all units in project are owner-occupied.
b. Option 1: Property owner pays 100% of the property’s utility bills and uses these bills as the source for tracking whole-property utility data in the online platform.
c. Option 2: Property owner requests, uploads, and tracks aggregated whole-property utility data from utility providers.
d. Option 3: Property owner collects 100% of the individual tenant-paid utility data from utility providers or tenants and tracks these as well as owner-paid accounts in the online platform.
e. Option 4: Property owner collects a sample of individual tenant-paid utility data from utility providers or tenants, which is then used to produce an estimate of whole-property utility data as well as owner-paid accounts. To extrapolate the whole-building data from the sample set, teams may use either 1) the Better Buildings Challenge sampling protocol, found in Appendix C of the Better Buildings Challenge Data Manual, OR 2) HUD’s Assisted Housing Utility Allowance Calculations sampling protocol, found in Part VI of HUD Notice H-2015-04.
i. When using sample tenant-paid utility data to estimate whole-property data, the “Estimation” box must be checked when submitting the data in ENERGY STAR Portfolio Manager.

[bookmark: _Toc233209877]01 91 00 / Commissioning
Part 1 - General
1.1  Summary
1. Related Sections
52. Section 01 81 13  Sustainability Requirements
1.2 Submittals
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
53. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
1. 2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
54. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
Part 2 - Products				
2.1 Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
Part 3 - Execution				
3.1 Execution Requirements		
1. 2026 Green Communities Criterion 7.1 Clean Air: Radon Testing and Mitigation	
56. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
1. 2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
57. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
[bookmark: _Toc233209878]01 92 13 / Facility Operation Procedures		
Part 1 - General				
1.1 Summary		
1. Related Sections
58. Section 01 81 13 Sustainability Requirements
1.2 Submittals		
1. 2026 Green Communities Criterion 8.1 Building Operations and Maintenance Manual and Plan
1. Submit documentation in accordance with 01 81 13 under Criterion 8.1.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution (no Green Communities Requirements)			
				
[bookmark: _Toc233209879]01 93 13 / Facility Maintenance Procedures		
Part 1 - General				
1.1 Summary		
1. Related Sections
60. Section 01 81 13 Sustainability Requirements
1.2 Submittals		
1. 2026 Green Communities Criterion 8.1 Building Operations and Maintenance Manual and Plan
1. Submit documentation in accordance with 01 81 13 under Criterion 8.1.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution (no Green Communities Requirements)			
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[bookmark: _Toc233209881]02 22 00 / Existing Conditions Assessment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements		
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 2.10: Adaptive Reuse of Buildings	
63. Conform to execution requirements in accordance with 01 81 13 under Criterion 2.10.
				
[bookmark: _Toc233209882]02 25 29 / Existing Thermal and Moisture Protection Assessment		
Part 1 - General				
1.1  Summary		
1. Related Sections		
64. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation
65. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation
66. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b.
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.3 Reduction of Lead Hazards in Pre-1978 Buildings
1. Submit documentation in accordance with 01 81 13 under Criterion 6.3.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 6.3 Reduction of Lead Hazards in Pre-1978 Buildings	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.3.
				
[bookmark: _Toc233209884]02 40 00 / Demolition and Structure Moving		
Part 1 - General				
1.1  Summary		
1. Related Sections	
70. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy F (Salvage Assessment)
71. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy F (Salvage Assessment)
72. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
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Part 1 - General				
1.1  Summary		
1. Related Sections	
73. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy F (Salvage Assessment)
74. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy F (Salvage Assessment)
75. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
				
[bookmark: _Toc233209886]02 41 19 / Selective Demolition		
Part 1 - General				
1.1  Summary		
1. Related Sections	
76. Section 01 81 13 Sustainable Building Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy F (Salvage Assessment)
1. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy F (Salvage Assessment).
2026 Green Communities Criterion 6.2 Reduction of Materials and Waste - Strategy I (End-of-use guidance)
2. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy I (End-of-use guidance)
2026 Green Communities Criterion 6.2 Reduction of Materials and Waste - Strategy J (Producer Responsibility Program)
3. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy J (Producer Responsibility Program)
2026 Green Communities Criterion 6.2 Reduction of Materials and Waste - Strategy K (Disassembly)
4. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy K (Disassembly)
2026 Green Communities Criterion 6.2 Reduction of Materials and Waste - Strategy L (Modular Design for Disassembly)
5. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy L (Modular Design for Disassembly).
Part 2 - Products				
2.1 Product Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy J (Producer Responsibility Program)
1. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy J (Producer Responsibility Program).
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy L (Modular Design for Disassembly)
2. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy L (Modular Design for Disassembly).
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criteria 2.10: Adaptive Reuse of Buildings
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 2.10.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy F (Salvage Assessment)
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy F (Salvage Assessment).
2026 Green Communities Criterion 6.2 Reduction of Materials and Waste - Strategy I (End-of-use guidance)
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy I (End-of-use guidance)
2026 Green Communities Criterion 6.2 Reduction of Materials and Waste - Strategy J (Producer Responsibility Program)
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy J (Producer Responsibility Program)
2026 Green Communities Criterion 6.2 Reduction of Materials and Waste - Strategy K (Disassembly)
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy K (Disassembly)
2026 Green Communities Criterion 6.2 Reduction of Materials and Waste - Strategy L (Modular Design for Disassembly)
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy L (Modular Design for Disassembly).
				
[bookmark: _Toc233209887]02 83 00 / Lead Remediation		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
2. Section 02 26 26 Lead Assessment
3. Section 02 83 19 Lead-Based Paint Remediation
4. Section 02 83 33 Removal and Disposal of Material Containing Lead
1.2  Submittals		
1. 2026 Green Communities Criterion 6.3 Reduction of Lead Hazards in Pre-1978 Buildings
81. Submit documentation in accordance with 01 81 13 under Criterion 6.3.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 6.3 Reduction of Lead Hazards in Pre-1978 Buildings	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.3.
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
2. Section 02 26 26 Lead Assessment
3. Section 02 83 00 Lead Remediation
4. Section 02 83 33 Removal and Disposal of Material Containing Lead
1.2  Submittals		
1. 2026 Green Communities Criterion 6.3 Reduction of Lead Hazards in Pre-1978 Buildings	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.3.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 6.3 Reduction of Lead Hazards in Pre-1978 Buildings	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.3.
				
[bookmark: _Toc233209889]02 83 33 / Removal and Disposal of Material Containing Lead		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
2. Section 02 26 26 Lead Assessment
3. Section 02 83 00 Lead Remediation
4. Section 02 83 19 Lead-Based Paint Remediation
1.2  Submittals		
1. 2026 Green Communities Criterion 6.3 Reduction of Lead Hazards in Pre-1978 Buildings	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.3.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 6.3 Reduction of Lead Hazards in Pre-1978 Buildings	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.3.
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[bookmark: _Toc233209891]03 11 19 / Insulating Concrete Forming		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9 Resilient Site Design: Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9, Option 2.
2026 Green Communities Criterion 6.4 Advanced Material Selection - Concrete	
2. Submit documentation in accordance with 01 81 13 under Criterion 6.4, Concrete.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9 Resilient Site Design: Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9, Option 2.
2026 Green Communities Criterion 6.4 Advanced Material Selection - Concrete	
2. Provide products in accordance with 01 81 13 under Criterion 6.4, Concrete.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9 Resilient Site Design: Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9, Option 2.
				
[bookmark: _Toc233209892]03 30 00 / Cast-in-Place Concrete		
Part 1 - General				
1.1  Summary		
1. Related Sections	
93. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy A (Right-size the structural system)
94. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy A (Right-size the structural system).
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Concrete
95. Submit documentation in accordance with 01 81 13 under Criterion 6.4, Concrete.
1. 2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
96. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1: Product Category Screening
97. Provide products in accordance with 01 81 13 under Criterion 6.1.
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Concrete
98. Provide products in accordance with 01 81 13 under Criterion 6.4, Concrete.
1. 2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
99. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy A (Right-size the structural system)
100. Conform to execution requirements in accordance with 01 81 13 under Criterion 
1. 2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
101. Conform to execution requirements in accordance with 01 81 13 under Criterion 
				
[bookmark: _Toc233209893]03 40 00 / Precast Concrete		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy A (Right-size the structural system)
1. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy A (Right-size the structural system).
2026 Green Communities Criterion 6.4: Advanced Material Selection - Concrete
2. Submit documentation in accordance with 01 81 13 under Criterion 6.4, Concrete.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
3. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1: Product Category Screening
1. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Concrete
2. Provide products in accordance with 01 81 13 under Criterion 6.4, Concrete.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
3. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy A (Right-size the structural system)
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 
				
[bookmark: _Toc233209894]03 70 00 / Mass Concrete		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy A (Right-size the structural system)
1. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy A (Right-size the structural system).
2026 Green Communities Criterion 6.4: Advanced Material Selection - Concrete
2. Submit documentation in accordance with 01 81 13 under Criterion 6.4, Concrete.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
3. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1: Product Category Screening
1. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Concrete
2. Provide products in accordance with 01 81 13 under Criterion 6.4, Concrete.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
3. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste - Strategy A (Right-size the structural system)
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure: New Construction
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9, Option 2.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Provide products in accordance with 01 81 13 under Criterion 3.9, Option 2.
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9, Option 2.
				
[bookmark: _Toc233209897]04 21 00 / Clay Masonry Units		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9, Option 2.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Provide products in accordance with 01 81 13 under Criterion 3.9, Option 2.
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9, Option 2.
				
[bookmark: _Toc233209898]04 22 00 / Concrete Unit Masonry		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9, Option 2.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Provide products in accordance with 01 81 13 under Criterion 3.9, Option 2.
2026 Green Communities Criterion 6.1: Product Category Screening	
2. Provide products in accordance with 01 81 13 under Criterion 6.1.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind (Option 2)	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9, Option 2.
				
				


[bookmark: _Toc233209899]Division 5: Metals				
[bookmark: _Toc233209900]05 10 00 / Structural Metal Framing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
				
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.2 - Strategy A (Right-size the structural system).
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2 - Strategy A (Right-size the structural system).
				
[bookmark: _Toc233209901]05 12 00 / Structural Steel Framing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Steel	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Steel	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution (no Green Communities Requirements)			
				
[bookmark: _Toc233209902]05 21 00 / Steel Joist Framing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Steel	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1 Product Category Screening	
1. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Steel	
2. Provide products in accordance with 01 81 13 under Criterion 6.4
Part 3 - Execution (no Green Communities Requirements)			
				
[bookmark: _Toc233209903]05 30 00 / Metal Decking		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Provide products in accordance with 01 81 13 under Criterion 3.11.
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
[bookmark: _Toc233209904]05 31 00 / Steel Decking		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Steel	
2. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.1: Product Category Screening	
2. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Steel	
3. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design: Wildfire	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
[bookmark: _Toc233209905]05 36 00 / Composite Metal Decking		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Provide products in accordance with 01 81 13 under Criterion 3.11.
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
[bookmark: _Toc233209906]05 40 00 / Cold-Formed Metal Framing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Steel	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Steel	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution (no Green Communities Requirements)			
				
[bookmark: _Toc233209907]05 52 00 / Metal Railings		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities
1. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy K (accessible thresholds).
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy K (accessible thresholds).
				
				


[bookmark: _Toc233209908]Division 6: Wood, Plastics, and Composites				
[bookmark: _Toc233209909]06 05 23 / Wood, Plastic, and Composite Fastenings		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Adhesives	
3. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Adhesives	
3. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
				
[bookmark: _Toc233209910]06 05 73 / Wood Treatment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
Part 3 - Execution				
3.1  Execution Requirements		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
[bookmark: _Toc233209911]06 05 83 / Shop-Applied Wood Coatings		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Paint/coatings	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection - Paint/coatings	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution (no Green Communities Requirements)			
				
[bookmark: _Toc233209912]06 10 00 / Rough Carpentry		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design For All Ages and Abilities, Strategy K	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy K (accessible thresholds).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.1: Product Category Screening	
2. Provide products in accordance with 01 81 13 under Criterion 6.1.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design For All Ages and Abilities, Strategy K	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14.
				
[bookmark: _Toc233209913]06 11 00 / Wood Framing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategies A, C, and D (as applicable).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 6.1: Product Category Screening	
3. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
4. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy D.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategies A, C, and D (as applicable).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design For All Ages and Abilities	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy K (accessible thresholds) and Strategy N (Doorway width), as applicable.
				
[bookmark: _Toc233209914]06 12 00 / Structural Panels		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 9.3.
				
[bookmark: _Toc233209915]06 15 00 / Wood Decking		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.1: Product Category Screening	
3. Provide products in accordance with 01 81 13 under Criterion 6.1.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
[bookmark: _Toc233209916]06 16 00 / Sheathing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 6.1: Product Category Screening	
3. Provide products in accordance with 01 81 13 under Criterion 6.1.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
				
[bookmark: _Toc233209917]06 16 26 / Underlayment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
				
[bookmark: _Toc233209918]06 17 53 / Shop-Fabricated Wood Trusses		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
				
[bookmark: _Toc233209919]06 20 00 / Finish Carpentry		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Wood, composite	
2. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1: Product Category Screening	
1. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
2. Provide products in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection - Wood, composite	
3. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Waste and Materials	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
				
[bookmark: _Toc233209920]06 41 93 / Cabinet and Drawer Hardware		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design For All Ages and Abilities	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.14 Strategy L (Handles and controls).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design For All Ages and Abilities	
1. Provide products in accordance with 01 81 13 under Criterion 7.14 Strategy L (Handles and controls).
Part 3 - Execution (no Green Communities Requirements)			
				
[bookmark: _Toc233209921]06 43 00 / Wood Stairs and Railings		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products (no Green Communities Requirements)	
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design For All Ages and Abilities	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14 Strategy K (Accessible thresholds).
				
[bookmark: _Toc233209922]06 45 20 / Exterior Trim		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
				
[bookmark: _Toc233209923]06 48 00 / Wood Frames		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1: Product Category Screening	
1. Provide products in accordance with 01 81 13 under Criterion 6.1.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety
202. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13 Strategy C (Stagger entry doors).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design For All Ages and Abilities	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14 Strategy N (Doorway width).
				
				
[bookmark: _Toc233209924]
Division 7: Thermal and Moisture Protection
[bookmark: _Toc233209925]07 10 00 / Dampproofing and Waterproofing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b
				
[bookmark: _Toc233209926]07 20 00 / Thermal Protection		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion  5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
4. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.1: Product Category Screening	
4. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
5. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
				
[bookmark: _Toc233209927]07 21 00 / Thermal Insulation		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.10.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
2. Submit documentation in accordance with 01 81 13 under Criterion  5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
5. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
6. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
2. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
3. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
4.  Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.1: Product Category Screening	
5. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
6. Provide products in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
7. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion  5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
4. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
5. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
6. Submit documentation in accordance with 01 81 13 under Criterion 7.3.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.1: Product Category Screening	
4. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
5. Provide products in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
6. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
7. Provide products in accordance with 01 81 13 under Criterion 7.3.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.3.
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
3. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
3.  Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
4. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1.  Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
3. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
4. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
5. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
6. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
7. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
8. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
3. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
4. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
5. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
6. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
7. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
3. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
4. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
5. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
6. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
7. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
8. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
3. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
4. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.1: Product Category Screening	
5. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
6. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
7. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
7. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
				
[bookmark: _Toc233209936]07 60 00 / Flashing and Sheet Metal		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
3. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1.  Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
3.  Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution (no Green Communities Requirements)			
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Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
2. Submit documentation in accordance with 01 81 13 under Criterion  5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
5. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
6. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
7. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
8. Submit documentation in accordance with 01 81 13 under Criterion 7.13.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
9. Submit documentation in accordance with 01 81 13 under Criterion 7.14
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
2. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
3. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
4. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
5. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
6. Provide products in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
7. Provide products in accordance with 01 81 13 under Criterion 7.14.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
7. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
8. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
9. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14.
				
[bookmark: _Toc233209942]08 17 00 / Integrated Door Opening Assemblies		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
				
[bookmark: _Toc233209943]08 30 00 / Specialty Doors and Frames		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
				
[bookmark: _Toc233209944]08 32 00 / Sliding Glass Doors		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
				
[bookmark: _Toc233209945]08 34 56 / Security Gates		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.13.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13.
				
[bookmark: _Toc233209946]08 40 00 / Entrances, Storefronts, and Curtain Walls		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.13.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13.
				
[bookmark: _Toc233209947]08 50 00 / Windows		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion  3.11.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
3. Submit documentation in accordance with 01 81 13 under Criterion  5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
5. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
6. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
7. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
8. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
2026 Green Communities Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	
9. Submit documentation in accordance with 01 81 13 under Criterion 7.12a.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
10. Submit documentation in accordance with 01 81 13 under Criterion 7.12b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
3. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
4. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
5. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
6. Provide products in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
7. Provide products in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	
8. Provide products in accordance with 01 81 13 under Criterion 7.12a.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
9. Provide products in accordance with 01 81 13 under Criterion 7.12b.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Advanced Material Selection	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
7. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
8. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
9. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.12b.
				
[bookmark: _Toc233209948]08 60 00 / Roof Windows and Skylights		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.9b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Provide products in accordance with 01 81 13 under Criterion 7.9a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.9a: Managing Moisture in the Building Enclosure - New Construction	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9a.
2026 Green Communities Criterion 7.9b: Managing Moisture in the Building Enclosure - Rehabilitation	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.9b.
				
[bookmark: _Toc233209949]08 71 00 / Door Hardware		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.3.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.13.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.14.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
2. Provide products in accordance with 01 81 13 under Criterion 7.3.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
3. Provide products in accordance with 01 81 13 under Criterion 7.13.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
4. Provide products in accordance with 01 81 13 under Criterion 7.14.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.3.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13.
				
[bookmark: _Toc233209950]08 74 00 / Access Control Hardware		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy F (Accessible Restroom).
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy F (Accessible Restroom).
				
[bookmark: _Toc233209951]08 80 00 / Glazing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
2. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.13.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.17.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
2. Provide products in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
3. Provide products in accordance with 01 81 13 under Criterion 7.17.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 6.2: Advanced Material Selection	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.17.
				
[bookmark: _Toc233209952]08 95 00 / Vents		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion  3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion  3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
				


[bookmark: _Toc233209953]Division 9: Finishes				
[bookmark: _Toc233209954]09 20 00 / Plaster and Gypsum Board		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
2. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 6.1: Product Category Screening	
2. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
3. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
				
[bookmark: _Toc233209955]09 28 00 / Backing Boards and Underlayments		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.10.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
2. Provide products in accordance with 01 81 13 under Criterion 7.10.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.10
				
[bookmark: _Toc233209956]09 28 13 / Cementitious Backing Boards		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.10.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Provide products in accordance with 01 81 13 under Criterion 7.10.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.10
				
[bookmark: _Toc233209957]09 30 00 / Tiling		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.10.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1: Product Category Screening	
1. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
2. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
3. Provide products in accordance with 01 81 13 under Criterion 7.10.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
4. Provide products in accordance with 01 81 13 under Criterion 7.15.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.10
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15
				
[bookmark: _Toc233209958]09 60 00 / Flooring		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
2. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.10.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.14.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
6. Submit documentation in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
7. Submit documentation in accordance with 01 81 13 under Criterion 7.17.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1: Product Category Screening	
1. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
2. Provide products in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
3. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
4. Provide products in accordance with 01 81 13 under Criterion 7.10.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
5. Provide products in accordance with 01 81 13 under Criterion 7.14.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
6. Provide products in accordance with 01 81 13 under Criterion 7.15.
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
7. Provide products in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
8. Provide products in accordance with 01 81 13 under Criterion 7.17.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.10.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15.
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
7. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.17.
				
[bookmark: _Toc233209959]09 65 13 / Resilient Base and Accessories		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
				
[bookmark: _Toc233209960]09 68 00 / Carpeting		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
				
[bookmark: _Toc233209961]09 70 00 / Wall Finishes		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.10.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.17.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
2. Provide products in accordance with 01 81 13 under Criterion 7.10.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Provide products in accordance with 01 81 13 under Criterion 7.15.
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
4. Provide products in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
5. Provide products in accordance with 01 81 13 under Criterion 7.17.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.10.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15.
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.17.
				
[bookmark: _Toc233209962]09 84 33 / Sound-Absorbing Wall Units		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.12a.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.12b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 7.12a.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 7.12b.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.12b.
				
[bookmark: _Toc233209963]09 84 36 / Sound-Absorbing Ceiling Units		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.12a.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.12b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 7.12a.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 7.12b.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.12b.
				
[bookmark: _Toc233209964]09 90 00 / Painting and Coating		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.10.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.1: Product Category Screening	
1. Provide products in accordance with 01 81 13 under Criterion 6.1.
2026 Green Communities Criterion 6.4: Advanced Material Selection	
2. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
3. Provide products in accordance with 01 81 13 under Criterion 7.10.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.10.
				
[bookmark: _Toc233209965]09 94 00 / Decorative Finishing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
2. Provide products in accordance with 01 81 13 under Criterion 7.15.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15.
				
				


[bookmark: _Toc233209966]Division 10: Specialties				
[bookmark: _Toc233209967]10 14 00 / Signage		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 2.6: Transit, Mobility, and Walkability	
1. Submit documentation in accordance with 01 81 13 under Criterion 2.6.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy A (if used).
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.17.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
1. Provide products in accordance with 01 81 13 under Criterion 7.14, Strategy A (if used).
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
2. Provide products in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
3. Provide products in accordance with 01 81 13 under Criterion 7.17.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 2.6: Transit, Mobility, and Walkability	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 2.6.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy A (if used).
2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.16.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.17.
				
[bookmark: _Toc233209968]10 28 00 / Toilet, Bath, and Laundry Accessories		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategies F, I and/or O (as applicable).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
1. Provide products in accordance with 01 81 13 under Criterion 7.14, Strategy A Strategies F, I and/or O (as applicable).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategies F, I and/or O (as applicable).
				
[bookmark: _Toc233209969]10 28 19 / Tub and Shower Enclosures		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.10.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Provide products in accordance with 01 81 13 under Criterion 7.10.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.10.
				
[bookmark: _Toc233209970]10 50 00 / Storage Specialties		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.13, Strategies G, I, and/or P (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Provide products in accordance with 01 81 13 under Criterion 7.13, Strategies G, I, and/or P (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13, Strategies G, I, and/or P (if used).
				
[bookmark: _Toc233209971]10 55 00 / Postal Specialties		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.13, Strategy I (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Provide products in accordance with 01 81 13 under Criterion 7.13, Strategy I (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13 Strategy I (if used).
				
[bookmark: _Toc233209972]10 71 00 / Exterior Protection		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
				
[bookmark: _Toc233209973]10 71 13 / Exterior Sun Control Devices		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.9: Passive Survivability	
2. Provide products in accordance with 01 81 13 under Criterion 5.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.9: Passive Survivability	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.9.
				
[bookmark: _Toc233209974]10 71 19 / Flood Barriers		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
				
[bookmark: _Toc233209975]10 73 00 / Protective Covers		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Provide products in accordance with 01 81 13 under Criterion 5.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.9.
				
[bookmark: _Toc233209976]10 81 00 / Pest Control Devices		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.11: Reducing Allergens and Disease Vectors - Integrated Pest Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.11
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.11: Reducing Allergens and Disease Vectors - Integrated Pest Management	
1. Provide products in accordance with 01 81 13 under Criterion 7.11.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.11: Reducing Allergens and Disease Vectors - Integrated Pest Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.11.
				
[bookmark: _Toc233209977]10 82 00 / Grilles and Screens		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Provide products in accordance with 01 81 13 under Criterion 5.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.9.
				
				


[bookmark: _Toc233209978]Division 11: Equipment				
[bookmark: _Toc233209979]11 30 00 / Residential Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy O (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy O (if used).
				
[bookmark: _Toc233209980]11 31 00 / Residential Appliances		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy O (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy O (if used).
				
[bookmark: _Toc233209981]11 60 00 / Entertainment and Recreation Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.17.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
1. Provide products in accordance with 01 81 13 under Criterion 7.17.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.17.
				
				


[bookmark: _Toc233209982]Division 12: Furnishings				
[bookmark: _Toc233209983]12 10 00 / Art		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.16.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
1. Provide products in accordance with 01 81 13 under Criterion 7.16.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.16: Healing-Centered and Culturally Responsive Design	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.16.
				
[bookmark: _Toc233209984]12 14 00 / Outdoor Sculpture and Ornamental Work		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Provide products in accordance with 01 81 13 under Criterion 7.15.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15.
				
[bookmark: _Toc233209985]12 20 00 / Window Treatments		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.9.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Provide products in accordance with 01 81 13 under Criterion 5.9.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.9: Passive Survivability	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.9.
				
[bookmark: _Toc233209986]12 30 00 / Casework		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy O (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Provide products in accordance with 01 81 13 under Criterion 6.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.4: Advanced Material Selection	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.4.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy O (if used).
				
[bookmark: _Toc233209987]12 36 00 / Countertops		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.10.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Provide products in accordance with 01 81 13 under Criterion 7.10.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.10: Managing Moisture - Bath, Kitchen, and Laundry Assemblies	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.10.
				
[bookmark: _Toc233209988]12 40 00 / Furnishings and Accessories		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.5: Recycling Storage	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.5.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy O (if used).
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.5: Recycling Storage	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.5.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy O (if used).
				
[bookmark: _Toc233209989]12 50 00 / Furniture		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategies D and/or G (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Provide products in accordance with 01 81 13 under Criterion 7.14, Strategy D (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategies D and/or G (if used).
				
[bookmark: _Toc233209990]12 92 33 / Interior Planters		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Provide products in accordance with 01 81 13 under Criterion 7.15.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15.
				
[bookmark: _Toc233209991]12 93 13 / Bicycle Racks and Wall Brackets		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 2.6: Transit, Mobility, and Walkability	
1. Submit documentation in accordance with 01 81 13 under Criterion 2.6, Increased Bikeability (if used).
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 2.6: Transit, Mobility, and Walkability	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 2.6, Increased Bikeability (if used).
				
				


[bookmark: _Toc233209992]Division 13: Special Construction				
[bookmark: _Toc233209993]13 12 00 / Fountains		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.15, Water Features (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Provide products in accordance with 01 81 13 under Criterion 7.15, Water Features (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15, Water Features (if used).
				
[bookmark: _Toc233209994]13 40 00 / Integrated Construction		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy D (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy D (if used).
				
[bookmark: _Toc233209995]13 42 00 / Building Modules		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy D (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy D (if used).
				
				


[bookmark: _Toc233209996]Division 14: Conveying Equipment				
[bookmark: _Toc233209997]14 91 82 / Trash Chutes		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 6.5: Recycling Storage	
1. Submit documentation in accordance with 01 81 13 under Criterion 6.5.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 6.5: Recycling Storage	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.5.
				
				


[bookmark: _Toc233209998]Division 22: Plumbing				
[bookmark: _Toc233209999]22 01 00 / Operation and Maintenance of Plumbing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 8.1: Building Operations and Maintenance Manual and Plan	
1. Submit documentation in accordance with 01 81 13 under Criterion 8.1.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution (no Green Communities Requirements)			
				
[bookmark: _Toc233210000]22 05 19 / Meters and Gauges for Plumbing Piping		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.4: Monitoring Water Consumption and Leaks	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.4.
2026 Green Communities Criterion 8.5: Energy and Water Data Collection and Monitoring	
2. Submit documentation in accordance with 01 81 13 under Criterion 8.5.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.4: Monitoring Water Consumption and Leaks	
1. Provide products in accordance with 01 81 13 under Criterion 4.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.4: Monitoring Water Consumption and Leaks	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.4.
2026 Green Communities Criterion 8.5: Energy and Water Data Collection and Monitoring	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 8.5.
				
[bookmark: _Toc233210001]22 07 00 / Plumbing Insulation		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.5.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
1. Provide products in accordance with 01 81 13 under Criterion 4.5.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.5.
				
[bookmark: _Toc233210002]22 09 00 / Instrumentation and Control for Plumbing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.5.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
1. Provide products in accordance with 01 81 13 under Criterion 4.5.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.5.
				
[bookmark: _Toc233210003]22 11 00 / Facility Water Distribution		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 4.1: Water-Conserving Fixtures	
2. Submit documentation in accordance with 01 81 13 under Criterion 4.1.
2026 Green Communities Criterion 4.2: Advanced Water Conservation	
3. Submit documentation in accordance with 01 81 13 under Criterion 4.2.
2026 Green Communities Criterion 4.3: Water Quality	
4. Submit documentation in accordance with 01 81 13 under Criterion 4.3.
2026 Green Communities Criterion 4.4: Monitoring Water Consumption and Leaks	
5. Submit documentation in accordance with 01 81 13 under Criterion 4.4.
2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
6. Submit documentation in accordance with 01 81 13 under Criterion 4.5.
2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
7. Submit documentation in accordance with 01 81 13 under Criterion 4.7.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
8. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 4.1: Water-Conserving Fixtures	
2. Provide products in accordance with 01 81 13 under Criterion 4.1.
2026 Green Communities Criterion 4.2: Advanced Water Conservation	
3. Provide products in accordance with 01 81 13 under Criterion 4.2.
2026 Green Communities Criterion 4.3: Water Quality	
4. Provide products in accordance with 01 81 13 under Criterion 4.3.
2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
5. Provide products in accordance with 01 81 13 under Criterion 4.5.
2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
6. Provide products in accordance with 01 81 13 under Criterion 4.7. 
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
7. Provide products in accordance with 01 81 13 under Criterion 5.2a.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 4.1: Water-Conserving Fixtures	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.1.
2026 Green Communities Criterion 4.3: Water Quality	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.3.
2026 Green Communities Criterion 4.4: Monitoring Water Consumption and Leaks	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.4.
2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.5.
2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.7.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
7. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
				
[bookmark: _Toc233210004]22 13 00 / Facility Sanitary Sewerage 		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 4.6: Indoor Water Efficiency - Nonpotable Water Reuse	
2. Submit documentation in accordance with 01 81 13 under Criterion 4.6.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 4.6: Indoor Water Efficiency - Nonpotable Water Reuse	
2. Provide products in accordance with 01 81 13 under Criterion 4.6.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
3. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
4. Provide products in accordance with 01 81 13 under Criterion 7.8.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.8.
				
[bookmark: _Toc233210005]22 14 00 / Storm Drainage		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.4: Surface Stormwater Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.4.
2026 Green Communities Criterion 3.6: Outdoor Water Use - Alternative Sources	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.6.
2026 Green Communities Criterion 4.6: Indoor Water Efficiency - Nonpotable Water Reuse	
3. Submit documentation in accordance with 01 81 13 under Criterion 4.6.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.6: Indoor Water Efficiency - Nonpotable Water Reuse	
1. Provide products in accordance with 01 81 13 under Criterion 4.6.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.4: Surface Stormwater Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.4.
2026 Green Communities Criterion 3.6: Outdoor Water Use - Alternative Sources	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.6.
				
[bookmark: _Toc233210006]22 31 16 / Ion-Exchange Water Treatment Systems		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.3.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Provide products in accordance with 01 81 13 under Criterion 4.3.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.3.
				
[bookmark: _Toc233210007]22 33 00 / Domestic Water Heaters		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.2.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Provide products in accordance with 01 81 13 under Criterion 7.2.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.2.
				
[bookmark: _Toc233210008]22 40 00 / Plumbing Fixtures		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.1: Water-Conserving Fixtures	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.1.
2026 Green Communities Criterion 4.2: Advanced Water Conservation	
2. Submit documentation in accordance with 01 81 13 under Criterion 4.2.
2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
3. Submit documentation in accordance with 01 81 13 under Criterion 4.5.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
5. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
6. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
2026 Green Communities Criterion 7.13: Personal and Social Safety	
7. Submit documentation in accordance with 01 81 13 under Criterion 7.13, Strategy H (if used).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
8. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategies G, J, L, and/or O (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.1: Water-Conserving Fixtures	
1. Provide products in accordance with 01 81 13 under Criterion 4.1.
2026 Green Communities Criterion 4.2: Advanced Water Conservation	
2. Provide products in accordance with 01 81 13 under Criterion 4.2.
2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
3. Provide products in accordance with 01 81 13 under Criterion 4.5.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
4. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
5. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
6. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
7. Provide products in accordance with 01 81 13 under Criterion 7.14, Strategies J and/or L (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.1: Water-Conserving Fixtures	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.1.
2026 Green Communities Criterion 4.5: Efficient Plumbing Layout and Design	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.5.
2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
2026 Green Communities Criterion 7.13: Personal and Social Safety	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13, Strategy H (if used).
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
7. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategies G and/or O (if used).
				
[bookmark: _Toc233210009]22 67 19.16 / Reverse-Osmosis Water Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.3.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Provide products in accordance with 01 81 13 under Criterion 4.3.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.3.
				
				


[bookmark: _Toc233210010]Division 23: HVAC				
[bookmark: _Toc233210011]23 01 00 / Operation and Maintenance of HVAC Systems		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.7.
2026 Green Communities Criterion 8.1: Building Operations and Maintenance Manual and Plan	
3. Submit documentation in accordance with 01 81 13 under Criterion 8.1.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Provide products in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Provide products in accordance with 01 81 13 under Criterion 7.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.7.
				
[bookmark: _Toc233210012]23 05 93 / Testing, Adjusting, and Balancing for HVAC		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Provide products in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Provide products in accordance with 01 81 13 under Criterion 7.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.7.
				
[bookmark: _Toc233210013]23 07 13 / Duct Insulation		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
2. Provide products in accordance with 01 81 13 under Criterion 5.3.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
				
[bookmark: _Toc233210014]23 08 00 / Commissioning of HVAC		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Provide products in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Provide products in accordance with 01 81 13 under Criterion 7.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.7.
				
[bookmark: _Toc233210015]23 09 00 / Instrumentation and Control for HVAC		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.13, Strategy F (if used).
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13, Strategy F (if used).
				
[bookmark: _Toc233210016]23 30 00 / HVAC Air Distribution		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.3.
2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.5.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
4. Provide products in accordance with 01 81 13 under Criterion 7.3.
2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
5. Provide products in accordance with 01 81 13 under Criterion 7.5.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
2026 Green Communities Criterion 7.3: Clean Air - Garage Isolation and Vehicle Pollution Management	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.3.
2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.5.
				
[bookmark: _Toc233210017]23 34 00 / HVAC Fans		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.5.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Provide products in accordance with 01 81 13 under Criterion 7.5.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.5.
				
[bookmark: _Toc233210018]23 38 00 / Ventilation Hoods		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.5.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Provide products in accordance with 01 81 13 under Criterion 7.5.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.5: Clean Air - Ventilation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.5.
				
[bookmark: _Toc233210019]23 40 00 / HVAC Air Cleaning Devices		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.6: Clean Air - Indoor Air Filtration	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.6.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.6: Clean Air - Indoor Air Filtration	
1. Provide products in accordance with 01 81 13 under Criterion 7.6.
2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
2. Provide products in accordance with 01 81 13 under Criterion 7.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.7: Clean Air - Enhanced IAQ	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.7.
				
[bookmark: _Toc233210020]23 51 00 / Breechings, Chimneys, and Stacks		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
2. Provide products in accordance with 01 81 13 under Criterion 7.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.5.
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.7.
				
[bookmark: _Toc233210021]23 52 00 / Boilers		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.2.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Provide products in accordance with 01 81 13 under Criterion 7.2.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.2.
				
[bookmark: _Toc233210022]23 54 00 / Furnaces		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Submit documentation in accordance with 01 81 13 under Criterion 7.2.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Provide products in accordance with 01 81 13 under Criterion 7.2.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.2.
				
[bookmark: _Toc233210023]23 70 00 / Central HVAC Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
2. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
3. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
				
[bookmark: _Toc233210024]23 72 00 / Air-to-Air Energy Recovery Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
1. Provide products in accordance with 01 81 13 under Criterion 7.8.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.8.
				
[bookmark: _Toc233210025]23 80 00 / Decentralized HVAC Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Provide products in accordance with 01 81 13 under Criterion 5.3.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.2a: Building Performance - New Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2a.
2026 Green Communities Criterion 5.2b: Building Performance - Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.2b.
2026 Green Communities Criterion 5.3: Advanced Building Performance	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.3
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
				
[bookmark: _Toc233210026]23 84 00 / Humidity Control Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
1. Provide products in accordance with 01 81 13 under Criterion 7.8.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.8.
				
				


[bookmark: _Toc233210027]Division 26: Electrical				
[bookmark: _Toc233210028]26 01 00 / Operation and Maintenance of Electrical Systems		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 8.1: Building Operations and Maintenance Manual and Plan	
1. Submit documentation in accordance with 01 81 13 under Criterion 8.1.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution (no Green Communities Requirements)			
				
[bookmark: _Toc233210029]26 05 19 / Low-Voltage Electrical Power Conductors and Cables		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.8.
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
1. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
2. Provide products in accordance with 01 81 13 under Criterion 7.8.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.8.
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.8.
				
[bookmark: _Toc233210030]26 05 33 / Raceway and Boxes for Electrical Systems		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1.  Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.8.
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
1. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
2. Provide products in accordance with 01 81 13 under Criterion 7.8.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.8.
2026 Green Communities Criterion 7.8: Managing Moisture - Dehumidification	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.8.
				
[bookmark: _Toc233210031]26 09 00 / Instrumentation and Control for Electrical Systems		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.5: Peak Demand Control	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.5.
2026 Green Communities Criterion 5.6: Backup Power	
2.  Submit documentation in accordance with 01 81 13 under Criterion 5.6.
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 5.5: Peak Demand Control	
1. Provide products in accordance with 01 81 13 under Criterion 5.5.
2026 Green Communities Criterion 5.6: Backup Power	
2. Provide products in accordance with 01 81 13 under Criterion 5.6.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.6: Backup Power	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.6.
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.8.
				
[bookmark: _Toc233210032]26 09 23 / Lighting Control Devices		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.3: Exterior Lighting	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.3
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategies C and/or L (if used).
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.3: Exterior Lighting	
1. Provide products in accordance with 01 81 13 under Criterion 3.3.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
2. Provide products in accordance with 01 81 13 under Criterion 7.14, Strategies C and/or L (if used).
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Provide products in accordance with 01 81 13 under Criterion 7.15.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.3: Exterior Lighting	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.3.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy C (if used).
				
[bookmark: _Toc233210033]26 24 16 / Panelboards		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Provide products in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.10: Resilient Site Design - Flood	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.10.
2026 Green Communities Criterion 5.4: All-Electric and Electric-Ready Design - New Construction/Rehabilitation	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.4a/b (as applicable).
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.8.
				
[bookmark: _Toc233210034]26 26 53 / Electrical Vehicle Charging Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
2. Submit documentation in accordance with 01 81 13 under Criterion 5.8.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.8.
				
[bookmark: _Toc233210035]26 27 00 / Low-Voltage Distribution Equipment		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
1. Submit documentation in accordance with 01 81 13 under Criterion 5.8.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategies C and/or L (if used).
2026 Green Communities Criterion 8.5: Energy and Water Data Collection and Monitoring	
3. Submit documentation in accordance with 01 81 13 under Criterion 8.5.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
1. Provide products in accordance with 01 81 13 under Criterion 7.14, Strategies C and/or L (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 5.8: Electric Vehicle Charging	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.8.
2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy C (if used).
2026 Green Communities Criterion 8.5: Energy and Water Data Collection and Monitoring	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 8.5.
				
[bookmark: _Toc233210036]26 30 00 / Facility Electrical Power Generating and Storing Equipment
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2.  Submit documentation in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.6: Backup Power	
3. Submit documentation in accordance with 01 81 13 under Criterion 5.6.
2026 Green Communities Criterion 5.7: Renewable Energy	
4. Submit documentation in accordance with 01 81 13 under Criterion 5.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
1. Provide products in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.6: Backup Power	
2. Provide products in accordance with 01 81 13 under Criterion 5.6.
2026 Green Communities Criterion 5.7: Renewable Energy	
3. Provide products in accordance with 01 81 13 under Criterion 5.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.9: Resilient Site Design - Wind	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.9.
2026 Green Communities Criterion 5.6: Backup Power	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.6.
2026 Green Communities Criterion 5.7: Renewable Energy	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 5.7.
				
[bookmark: _Toc233210037]26 50 00 / Lighting		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1.  Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.3: Exterior Lighting	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.3
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
2. Submit documentation in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
4. Submit documentation in accordance with 01 81 13 under Criterion 7.17.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.3: Exterior Lighting	
1. Provide products in accordance with 01 81 13 under Criterion 3.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
2. Provide products in accordance with 01 81 13 under Criterion 6.2.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Provide products in accordance with 01 81 13 under Criterion 7.15.
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
4. Provide products in accordance with 01 81 13 under Criterion 7.17.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.3: Exterior Lighting	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.3.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
2026 Green Communities Criterion 7.17: Active Design - Promoting Physical Activity	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.17.				
[bookmark: _Toc233210038]Division 27: Communications				
[bookmark: _Toc233210039]27 10 00 / Structured Cabling		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 2.9: Access to Broadband	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 2.9.
				
[bookmark: _Toc233210040]27 20 00 / Data Communications		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.14, Strategy G (if used).
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.14: Social Connection and Accessibility - Design for All Ages and Abilities	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.14, Strategy G (if used).
				
				


[bookmark: _Toc233210041]Division 28: Electronic Safety & Security				
[bookmark: _Toc233210042]28 10 00 / Electronic Access Control and Intrusion Detection		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Provide products in accordance with 01 81 13 under Criterion 7.13, Strategy D (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion  7.13, Strategy D (if used).
				
[bookmark: _Toc233210043]28 13 00 / Access Control		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.13, Strategy G (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Provide products in accordance with 01 81 13 under Criterion 7.13, Strategy D (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion  7.13, Strategies D and/or G (if used).
				
[bookmark: _Toc233210044]28 31 49 / Carbon-Monoxide Detection Sensors		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.2.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
1. Provide products in accordance with 01 81 13 under Criterion 7.2.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.2: Clean Air - Combustion Equipment	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.2.
				
[bookmark: _Toc233210045]28 45 00 / Water Detection and Alarm		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.4: Monitoring Water Consumption and Leaks	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.4.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.4: Monitoring Water Consumption and Leaks	
1. Provide products in accordance with 01 81 13 under Criterion 4.4.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.4: Monitoring Water Consumption and Leaks	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.4.
				
				


[bookmark: _Toc233210046]Division 31: Earthwork				
[bookmark: _Toc233210047]31 10 00 / Site Clearing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.1: Minimization of Disturbance During Staging and Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.1.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.1: Minimization of Disturbance During Staging and Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.1.
				
[bookmark: _Toc233210048]31 21 13 / Radon Mitigation		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.1: Clean Air: Radon Testing and Mitigation	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.1.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.1: Clean Air: Radon Testing and Mitigation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.1.
				
[bookmark: _Toc233210049]31 25 00 / Soil Erosion and Sedimentation Controls		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.1: Minimization of Disturbance During Staging and Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.1.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.1: Minimization of Disturbance During Staging and Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.1.
				
[bookmark: _Toc233210050]31 31 19 / Vegetation Control		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.13, Strategy E (if used).
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Provide products in accordance with 01 81 13 under Criterion 7.15.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.13: Personal and Social Safety	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13, Strategy E (if used).
				
				


[bookmark: _Toc233210051]Division 32: Exterior Improvements				
[bookmark: _Toc233210052]32 12 00 / Flexible Paving		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
				
[bookmark: _Toc233210053]32 13 00 / Rigid Paving		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
				
[bookmark: _Toc233210054]32 14 00 / Unit Paving		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Submit documentation in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Provide products in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 6.2: Reduction of Materials and Waste	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 6.2, Strategy E (if used).
				
[bookmark: _Toc233210055]32 15 00 / Aggregate Surfacing		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Provide products in accordance with 01 81 13 under Criterion 3.11.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
[bookmark: _Toc233210056]32 16 00 / Cement Concrete Sidewalk, Curbs, and Gutters		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.7.
2026 Green Communities Criterion 3.8: Heat-Island Management	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.8: Heat-Island Management	
1. Provide products in accordance with 01 81 13 under Criterion 3.8.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.7.
2026 Green Communities Criterion 3.8: Heat-Island Management	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
				
[bookmark: _Toc233210057]32 16 13 / Curbs and Gutters		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 2.6: Transit, Mobility, and Walkability 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 2.6, Increased Walkability (if used). 
				
[bookmark: _Toc233210058]32 16 23 / Sidewalks		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 2.6: Transit, Mobility, and Walkability 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 2.6, Increased Walkability (if used). 
				
[bookmark: _Toc233210059]32 17 00 / Paving Specialties		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.7.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1.  Provide products in accordance with 01 81 13 under Criterion 3.11.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 2.6: Transit, Mobility, and Walkability 	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 2.6, Increased Walkability (if used). 
2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.7.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
[bookmark: _Toc233210060]32 17 29 / Crosswalk Warning Lights and Signs		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	2026 Green Communities Criterion 3.7: Traffic Safety and Mobility
1. Provide products in accordance with 01 81 13 under Criterion 3.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.7.
				
[bookmark: _Toc233210061]32 31 00 / Fences and Gates		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.7.
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Provide products in accordance with 01 81 13 under Criterion 3.7.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
3. Provide products in accordance with 01 81 13 under Criterion 7.13, Strategy D (if used).
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.7.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13, Strategy D (if used).
				
[bookmark: _Toc233210062]32 80 00 / Irrigation		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.5: Outdoor Water Use - Efficient Irrigation	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.5.
2026 Green Communities Criterion 3.6: Outdoor Water Use - Alternative Sources	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.6.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.5: Outdoor Water Use - Efficient Irrigation	
1. Provide products in accordance with 01 81 13 under Criterion 3.5.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.5: Outdoor Water Use - Efficient Irrigation	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.5.
2026 Green Communities Criterion 3.6: Outdoor Water Use - Alternative Sources	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.6.
				
[bookmark: _Toc233210063]32 90 00 /  Planting		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.4: Surface Stormwater Management	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.4.
2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
3. Submit documentation in accordance with 01 81 13 under Criterion 3.7.
2026 Green Communities Criterion 3.8: Heat-Island Management	
4. Submit documentation in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
5. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
6. Submit documentation in accordance with 01 81 13 under Criterion 7.13, Strategy E (if used).
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
7. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Provide products in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.8: Heat-Island Management	
2. Provide products in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
3. Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
4. Provide products in accordance with 01 81 13 under Criterion 7.15.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.4: Surface Stormwater Management	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.4.
2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.7.
2026 Green Communities Criterion 3.8: Heat-Island Management	
4. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.8.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
5. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.13: Personal and Social Safety	
6. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.13, Strategy E (if used).
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
7. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15.
				
[bookmark: _Toc233210064]32 91 13 / Soil Preparation		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.1: Minimization of Disturbance During Staging and Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.1.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.1: Minimization of Disturbance During Staging and Construction	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.1.
				
[bookmark: _Toc233210065]32 92 00 / Turf and Grasses		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.4: Surface Stormwater Management	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.4.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
3. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Provide products in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Provide products in accordance with 01 81 13 under Criterion 3.11.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.4: Surface Stormwater Management	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.4.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
				
[bookmark: _Toc233210066]32 93 00 /  Plants		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Provide products in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2.  Provide products in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Provide products in accordance with 01 81 13 under Criterion 7.15.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.2: Site Design for Ecosystem Services	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.2.
2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.11.
2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
3. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15.
				
[bookmark: _Toc233210067]32 94 33 / Planters		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.15.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.15: Access to Nature and Biophilic Design	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 7.15.
				
				


[bookmark: _Toc233210068]Division 33: Utilities				
[bookmark: _Toc233210069]33 05 01 / Lead Service Line Replacement		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.3.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Provide products in accordance with 01 81 13 under Criterion 4.3.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.3.
				
[bookmark: _Toc233210070]33 11 00 / Water Utility Distribution Piping 		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.3.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.3: Water Quality	
1. Provide products in accordance with 01 81 13 under Criterion 4.3.
Part 3 - Execution				
3.1  Execution Requirements			
2026 Green Communities Criterion 4.3: Water Quality	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.3.
				
[bookmark: _Toc233210071]33 16 00 / Water Storage Tanks		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.6: Outdoor Water Use - Alternative Sources	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.6.
2026 Green Communities Criterion 4.6: Indoor Water Efficiency - Nonpotable Water Reuse	
2. Submit documentation in accordance with 01 81 13 under Criterion 4.6.
2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
3. Submit documentation in accordance with 01 81 13 under Criterion 4.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.6: Indoor Water Efficiency - Nonpotable Water Reuse	
1. Provide products in accordance with 01 81 13 under Criterion 4.6.
2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
2. Provide products in accordance with 01 81 13 under Criterion 4.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.6: Outdoor Water Use - Alternative Sources	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.6.
2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.7.
				
[bookmark: _Toc233210072]33 21 00 / Water Supply Wells		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
1. Submit documentation in accordance with 01 81 13 under Criterion 4.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
1. Provide products in accordance with 01 81 13 under Criterion 4.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 4.7: Access to Potable Water During Emergencies	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 4.7.
				
[bookmark: _Toc233210073]33 49 00 / Storm Drainage Structures		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.4: Surface Stormwater Management	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.4.
2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
2. Submit documentation in accordance with 01 81 13 under Criterion 3.7.
Part 2 - Products (no Green Communities Requirements)			
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.4: Surface Stormwater Management	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.4.
2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
2. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.7.
				
				


[bookmark: _Toc233210074]Division 34: Transportation				
[bookmark: _Toc233210075]34 71 13 / Vehicle Barriers		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Submit documentation in accordance with 01 81 13 under Criterion 3.7.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 3.11: Resilient Site Design - Wildfire	2026 Green Communities Criterion 3.7: Traffic Safety and Mobility
1. Provide products in accordance with 01 81 13 under Criterion 3.7.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 3.7: Traffic Safety and Mobility	
1. Conform to execution requirements in accordance with 01 81 13 under Criterion 3.7.
				
				


[bookmark: _Toc233210076]Division 44: Pollution and Waste Control Equipment				
[bookmark: _Toc233210077]44 20 00 / Noise Pollution Control		
Part 1 - General				
1.1  Summary		
1. Related Sections	
1. Section 01 81 13 Sustainability Requirements
1.2  Submittals		
1. 2026 Green Communities Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	
1. Submit documentation in accordance with 01 81 13 under Criterion 7.12a.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
2. Submit documentation in accordance with 01 81 13 under Criterion 7.12b.
Part 2 - Products				
2.1  Product Requirements			
1. 2026 Green Communities Criterion 7.12a: Sensory and Rest Friendly - Noise Reduction, New Construction	
1. Provide products in accordance with 01 81 13 under Criterion 7.12a.
2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
2. Provide products in accordance with 01 81 13 under Criterion 7.12b.
Part 3 - Execution				
3.1  Execution Requirements			
1. 2026 Green Communities Criterion 7.12b: Sensory and Rest Friendly - Noise Reduction, Rehabilitation	
Conform to execution requirements in accordance with 01 81 13 under Criterion 7.12b.
				
				
