4.3 Water Quality Management Program Template

Effective April 2026

# How to Use This Template:

This document is a working template to help project teams develop a site-specific Water Quality and Legionella Management Program consistent with the 2026 Enterprise Green Communities Criterion 4.3. The template is intentionally editable. Project teams should adapt it to reflect the building’s water systems, scale, occupancy, operations, local codes, and applicable public health guidance. Content may be added, removed, or modified as appropriate for the project.

This template aligns with the Centers for Disease Control and Prevention (CDC) framework for developing a Legionella water management program and is designed to reduce the burden on project teams by translating CDC expectations into a practical, fill-in-ready format. It is not intended to prescribe a single approach or replace professional judgment, local requirements, or public health authority guidance.

Before completing this template, project teams are strongly encouraged to review the CDC Water Management Program Worksheet, which helps determine whether a building or specific systems present increased risk for Legionella and therefore require a water management program. The worksheet is available at: https://www.cdc.gov/control-legionella/php/toolkit/wmp-worksheet.html

# Section 1. Program Team

| Role | Name/Contact |
| --- | --- |
| Program Manager (Owner Rep) | Click or tap here to enter text. |
| Facilities/Engineering Lead | Click or tap here to enter text. |
| Water Treatment Consultant (if applicable) | Click or tap here to enter text. |
| Resident Services / Communication Lead | Click or tap here to enter text. |
| Other Key Contacts (e.g., Local Utility, Health Dept.) | Click or tap here to enter text. |

# Section 2. Building Information

- Building Name/Address: Click or tap here to enter text.

- Year Constructed: Click or tap to enter a date.

- Rehab Year (if applicable): Click or tap to enter a date.

- Lead Service Line Present: ☐ Yes ☐ No ☐ Unknown

- System Features (check all that apply):

- ☐ Centralized hot-water system

- ☐ Cooling tower

- ☐ Building with ≥10 stories

- ☐ Decorative fountains, spas, or other aerosolizing devices

# Section 3. System Mapping

Insert Flow Diagram(s): Click or tap here to enter text.

(Water entry → service lines → storage/heating → distribution loops → outlets → specialized equipment)

Attach annotated plumbing drawings where available.

# Section 4. Hazard Identification

| Hazard Type | Condition | Location(s) | Notes |
| --- | --- | --- | --- |
| Lead | Lead service line (pre-1986) | Click or tap here to enter text. | Replace during rehab |
| Lead | Leaded solder/fixtures | Click or tap here to enter text. | Replace with lead-free |
| Legionella | Stagnation (dead legs, low-use outlets) | Click or tap here to enter text. | Flush schedule required |
| Legionella | Temp in growth range (77–113°F) | Click or tap here to enter text. | Monitor heater & riser temps |
| Legionella | Inadequate disinfectant residual | Click or tap here to enter text. | Test for chlorine/chloramine |
| Legionella | Cooling tower / aerosol device | Click or tap here to enter text. | Requires biocide program |

# Section 5. Control Measures

| Hazard | Control Measure | Control Limit | Monitoring Frequency | Responsible Person |
| --- | --- | --- | --- | --- |
| Lead – service lines | Replace line | 100% replacement | During rehab | Contractor |
| Lead – fixtures | Replace w/ lead-free | 100% replacement | During rehab | Facilities |
| Hot water | Maintain ≥ 120°F (w/in code) | ≥ 120°F | Weekly | Facilities |
| Cold water | Maintain ≤ 77°F | ≤ 77°F | Quarterly | Facilities |
| Disinfectant | Maintain ≥ 0.2 ppm free chlorine (or local standard) | ≥ 0.2 ppm | Monthly | Vendor |
| Cooling tower | Maintain biocide treatment | Per O&M plan | Daily | Facilities/Vendor |

# Section 6. Monitoring, Verification & Validation

Monitoring: Record temp, disinfectant, tower logs, and lead replacement status.

Verification: Confirms that the Water Management Program is being implemented as written.

- Program Manager reviews logs monthly

Validation: Evaluates whether the program is effectively controlling conditions that could support lead contamination and/or Legionella growth and spread.

- Lead: EPA-approved sampling after replacement.

- Legionella: Environmental testing if indicated by CDC/ASHRAE.

# Section 7. Corrective Actions

Lead:

- If line/fixture identified → replace.

- If post-replacement sampling shows lead → re-flush, retest, escalate to utility.

Legionella:

- Out-of-range temp/disinfectant → adjust, flush, document.

- Cooling tower lapse → shut down until treatment restored.

- Positive Legionella test → implement remediation protocol (e.g., hyperchlorination).

# Section 8. Documentation & Communication

Program Review: This Water Management Program should be reviewed at least annually and updated following major building changes, prolonged vacancy, water quality disruptions, system modifications, or confirmed cases of Legionnaires’ disease.

- Maintain records of: system mapping & hazard analysis, monitoring logs & control results, corrective actions taken, verification & validation reviews.

- Annually: Update hazards, confirm controls effective, document results.

- Application Requirement: Submit program copy + implementation documentation.

# Section 9. Flow Chart (Example Structure)

[Municipal Water Entry]

↓

[Service Line] → (Lead risk check)

↓

[Water Heater / Storage] → (Temp & disinfectant monitoring)

↓

[Distribution Loops] → (Dead leg flushing / sampling)

↓

[Outlets / Fixtures] → (Resident-use monitoring)

↓

[Cooling Tower / Aerosol Devices] → (Treatment + biocide program)